## Sheet1
E-Procurement Schedule
Name of the Work: - Construction of Control Room, Retaining wall for Switch yard, Compound wall and Drilling of Borewell for Erection of new 33/11KV Outdoor Sub-Station at Vasavi Nagar, Boduppal Municipality, Habsiguda Division in Habsiguda Circle.
S.No | Estimate Qty | Description of the Item | Work Type eg. Earth Work, Electrical works.. etc ( Upto 200 Characters) | Item Short Description ( Upto 100 Characters) | APSS / Morth Cl. Number ( Upto 200 Characters) | Rate (INR) ( Upto 2 Decimals ) | UOM ( Upto 50 Characters) | Amount (INR) ( Upto 2 Decimals )
1 | 1 | Geophysical investigation charges | Geophysical investigation | Geophysical investigation | As per relevent standard specification | 5000 | EA | 5000 | EA | EA
2 | 90 | Drilling-165mm Bore Well 0 to 90M, Drilling of 6.5" dia bore well from ground level in all formations including cost and conveyance of all materials labour charges etc., complete for finished item of work. | Drilling borewell | Drilling borewell | As per relevent standard specification | 336 | M | 30240
3 | 30 | Drill-165mm Bore Well 90M to 120M | Drilling borewell | Drilling borewell | As per relevent standard specification | 369 | M | 11070
4 | 30 | Drill-165mm Bore Well 120 M to 150M | Drilling borewell | Drilling borewell | As per relevent standard specification | 394 | M | 11820
5 | 30 | Drill-165mm Bore Well 150M to 180M | Drilling borewell | Drilling borewell | As per relevent standard specification | 492 | M | 14760
6 | 20 | Suppy & fixing of 180 mm dia. 6 kg/cm2 PVC casing pipe including cost and conveyance of all materials labour charges etc complete for finished item of work. | PVC Casing | PVC Casing | As per relevent standard specification | 883 | M | 17660
7 | 200 | Supply and fixing of HDPE pipe 40mm dia. including cost and conveyance of all materials labour charges etc complete for finished item of work. | HDPE Pipe | HDPE Pipe | As per relevent standard specification | 180 | M | 36000
8 | 1 | Supply and Fixing of 1.5HP Texmo/Kirloskar make motor of single phase submersible of multiple stage including all materials and labour charges complete for finished item. | 1.5HP submersbile pump | 1.5HP submersbile pump | As per relevent standard specification | 29047 | EA | 29047
9 | 200 | Supply and fixing of 2.5mm single core copper cable complete for finished item. | Copper cable | Copper cable | As per relevent standard specification | 192 | M | 38400
10 | 1 | Supply and Fixing of Flange Clamps including cost and conveyance of all materials | Flange Clamps | Flange Clamps | As per relevent standard specification | 182 | EA | 182
11 | 1 | Supply and erecting D.O.L Starter 250V, Single phase, 50Hz with SS enclouser comprising of contactor with bi-metallic relay with necessary push buttons, transportation and all labour charges etc. complete. | Single phase starter | Single phase starter | As per relevent standard specification | 1040 | EA | 1040
12 | 24 | Hiring of JCB for site levelling and cleaning | Hiring of JCB | Hiring of JCB | As per relevent standard specification | 2165 | H | 51960
13 | 266.9 | Earth Work Mass Excavation to a depth as directed, in soils such as Mixture of Gravel and Soft Disintegrated Rock like Shales, Ordinary Gravel, Stoney Earth and Earth Mixed with Fair Sized Boulders and in all conditions such as dry, wet, slurry etc.and in dense or hard soils, disposal and depositing of excavated soil with intial lead of 10 mt and intial lift of 2m or as directed, including cost and conveyance of all materials, ramping and lifting of materials, and labour charges, hire charges of machinery, tools & plants, bailing of water (either sub soil water, storm water, rain water, surface water or of any kind) if any at any stage of work until all works below ground level is finished to the satisfaction ,and from work such as shoring, timbering, strutting with required supports etc. for the work and removal of form work after completion of work etc all complete | Earth Work Mass Excavation | Earth Work Mass Excavation | As per relevent standard specification | 486 | M3 | 129713.4
14 | 11 | Back Filling the foundation Columns, for lift wells ,Staircase foundation ,U.G Sump Septic tank, Road work ,storm water drain ,cable trench,soak pit and outside of hte reataining wall with the useful avilable excavated earth ,in layers not exceeding 150mm thick, conslidating each deposited layer by eatering and ramming including cost and conveyance of all materials labour chargess,hire charges of T&P,all leads and lifts etc,complete for finished item of work | Back Filling | Back Filling | As per relevent standard specification | 34 | M3 | 374
15 | 38 | Providing and laying Plain Cement concrete of (1:4:8) for levelling course using 40mm size hard broaken Granite stone including cost and conveyance of all materials, se HBG metal for foundations and leveling course, including cost and conveyance of all materials,seignorage, water, labour charges, hire charges of nachinery, at all levels, depths,heights and floors consolidation by watering ,ramming in layers,bailing of water if any, and removal of form work after completion of work curing for reqired number of days,all incidental charges etc complete for finished item of work. | PCC (1:4:8) 40mm metal | PCC (1:4:8) 40mm metal | As per relevent standard specification | 4887 | M3 | 185706
16 | 7 | Providing and laying Plain Cement Concrete of (1:2:4) with well graded machine crushed granite metal of 20mm nominal size from approved quarry for Bed Blocks, Hold Fasts including cost and conveyance of all materials, labour charges,hire charges of machnery,with all leads and lifts, for all floors curing for required number of days, all incidental charges etc complete for finished item work | PCC (1:2:4) 20mm metal | PCC (1:2:4) 20mm metal | As per relevent standard specification | 6304 | M3 | 44128
17 | 246 | CRS masonry in CM(1:6) using Hard Granite Stones including cost and conveyance of all materials, seignorage charges, labour charge for construction and for dressing stones to required size and shape, dewatering,scaffolding,cutting for all leads and lifts, all incidental charges etc .complete for finished item of work | CRS Masonary | CRS Masonary | As per relevent standard specification | 5018 | M3 | 1234428
18 | 744 | Supplying and filling with borrowed gravel, watering, ramming, consolidating thoroughly complying with the standard specification including cost and conveyance of all materials, labour charges,hire charges of machnery,with all leads and incidental charges etc complete for finished item work | filling with gravel | filling with gravel | As per relevent standard specification | 640 | M3 | 476160
19 | 5.2 | a)Footings, Ground floor, Reinforced Cement concerete M20 GRADE Nominal Mix for footings , columns, Beams and Slab using 12mm to 20mm size graded HBG machine crushed metal from approvaed quary giving cube crushing strenth of 20 N /sqmm and a minimum of 400 kgs of cement for 1 cum of concrete including cost and conveyance charges for cement and all other materials to site, scaffolding charge , seignorage charges, centering, shuttering, machine mixing,laying concrete, curing for specified number of days vibrating etc compaction by pen vibrator or needle vibrator supplemented by hand spreeding rodding and tamping ,all incident and operational charges , all leads and lifts and for all leaving gaps and pockets etc complete, but excuding cost of ssteel and its fabrication,all incidental charges etc .complete for finshed item of work | RCC Footings | RCC Footings | As per relevent standard specification | 9357 | M3 | 48656.4
20 | 3.7 | b)Columns | RCC Columns | RCC Columns | As per relevent standard specification | 12579 | M3 | 46542.3
21 | 2.15 | c)Plinth beams | RCC Plinth beams | RCC Plinth beams | As per relevent standard specification | 12002 | M3 | 25804.3
22 | 2.71 | d)Roof beams | RCC Roof beams | RCC Roof beams | As per relevent standard specification | 11965 | M3 | 32425.15
23 | 0.55 | e)Lintels | RCC Lintels | RCC Lintels | As per relevent standard specification | 12573 | M3 | 6915.15
24 | 3.4 | f)Sun shade 0.6m width 3" thick | RCC Sunshades | RCC Sunshades | As per relevent standard specification | 1306 | M2 | 4440.4
25 | 13.02 | g)Slab | RCC Slab | RCC Slab | As per relevent standard specification | 11035 | M3 | 143675.7
26 | 100 | A)Ground floor, Providing plastering of 20mm thick to all uneven faces of walls and ceiling of superstructure in two coats with base coat in CM 1:5of 16mm thick and top coat in Cm 1:3 4mm thick with dubara sponge finish including cost and conveyance of, Brick masonry for wall in superstructure (230mm thick) in CM 1:6 using traditional Local madeSecound Class Bricks from approved sourse and quality having crushing strength of not less than 100 Kg/sq cm and water absorption not exceeding 20% by weight including cost and conveyance of all mateerials, seigniorage charge, all labour charges, curing for number of days as specified, for all leads, lifts scaffolding chargess, at all heght levels and floors all incidental charges etc completed item of work. | Brick masonary | Brick masonary | As per relevent standard specification | 8182 | M3 | 818200
27 | 3.1 | Providing High Yield Strength Deformed (HYSD)/ Thermo Mechanically Treated (TMT) / Mild steel (MS) steel bars (Fe 415/ Fe 500 grade as per IS 1786-1979) of different diameters for RCC works , including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying and lap-splicing with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings, including cost and conveyance of steel bars, including all wastages such as overlaps, couplings, chairs, spacer bars including cost and conveyance of binding wire, cover blocks and all incidental, operational, labour charges such as cutting, bending, placing in position, tying including sales and other taxes on all materials etc.,complete for finished item of work | HYSD Steel | HYSD Steel | As per relevent standard specification | 78657 | MT | 243836.7
28 | 1168 | A)Ground floor, Providing plastering of 20mm thick to all uneven faces of walls and ceiling of superstructure in two coats with base coat in CM 1:5of 16mm thick and top coat in Cm 1:3 4mm thick with dubara sponge finish including cost and conveyance of all materials . water. all labour charges, curing for specified number of days, cutting grooves, at allheghits, level and floro, all leads, lifts and scaffolding charges, all incidental and scaffolding charges, seigniorage charges, all incidental charges etc. complete for finished item of work | Plastering 20mm thick | Plastering 20mm thick | As per relevent standard specification | 498 | M2 | 581664
29 | 315 | Raised pointing in CM(1:3) including curing, cost and conveyance of all materials and labour charges for complete item of work. | Raised pointing | Raised pointing | As per relevent standard specification | 113 | M2 | 35595
30 | 64.05 | Providing impervious coat over RCC roof slab surfaces to requried slopes with 20mm thick in CM 1:3 pro mixed with approved brand of water proofing compound as the rate of 1 kg per bag of cement including cost and conveyance of all materials, water, all labour charges, chemicals, curing for specifed number of days,rounding off junctions of wall and slab, all leads, lifts, heights,levels and floors etc.complete for finished item of work. | impervious coat | impervious coat | As per relevent standard specification | 524 | M2 | 33562.2
31 | 15 | Providing Reinforced cement Drop Walls in CM 1:2 of 40mm thick over rabbit wire mesh including cost and conveyance of all meterials, labour charges, curing for specified number of days,at all levels, floors, height, leads and lifts, seignioage charges all incidental charges etc . complete, but excluding cost of steel as per the approved drawing for finished item of work | RCM Drop Walls | RCM Drop Walls | As per relevent standard specification | 2953 | M2 | 44295
32 | 6 | Supply and fixing of doors with the frames of the door shall be made well seasoned MT wood of cross section 100x75mm. The shutter shall be made ISI mark flushed door with two coats of synthetic enamel paint of approved color over one coat of primer over luppum with spary on both sides with 3 no 150mm hinges, 1 no door stoper, 1 no 250mm aldrop, 1 no 300 mm tower bolts, 2 no 150mm door handlers of MS Powder coated, including cost and conveyance of the meterials,fixing,labour carges,tools,handles,locking arrangementts and other fixtures & fittings for finished item work | MT Wood Doors Shutter with frame | MT Wood Doors Shutter with frame | As per relevent standard specification | 7314 | M2 | 43884
33 | 5.8 | S&F-UPVC Sliding Windows of approved make including cost and coveyance of all mateirals with all leads and lifts, labour charges, painting charges complete for finished item of work | UPVC Sliding Windows | UPVC Sliding Windows | As per relevent standard specification | 6063 | M2 | 35165.4
34 | 6.8 | Supplying and fixing of MS safety grill with peripheral frame of ISA 25x25x4mm and 8mm square rods at 100mm c/c both in horizontal & vertical direction including cost and coveyance of all mateirals with all leads and lifts, labour charges, painting charges complete for finished item of work | MS safety grill | MS safety grill | As per relevent standard specification | 2990 | M2 | 20332
35 | 3.7 | Flooring with ceramic tiles of 1st class quality of approved brand shade and design of different size laid over a floor bed of CM 1:3 of 12 mm thick base coat and neat grey cement slurry of honey like consistancy spread at the ratet of 3.3 kg of cement per sqm and pointed to full deapth, (joints must be flushed) with white cement paste mixed with pigment when requied including cost and conveyance of cement and all materials ,labour charges, at all levels, heights and floors,curing etc. complete for finished item of work. | ceramic tiles flooring | ceramic tiles flooring | As per relevent standard specification | 844 | M2 | 3122.8
36 | 14.4 | Providing skirting to internal walls to 15 cm height/risers of steps with ceramic tile length equal to floor tile, set over base coat of CM (1:3) 12 mm thick with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointed with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like Shahabad stone, cement, sand and water etc., complete for finished item of work | ceramic tiles dadoing | ceramic tiles dadoing | As per relevent standard specification | 979 | M2 | 14097.6
37 | 40 | Flooring with polished shabads stone quality and approved size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and pointing with cement, labour etc, complete | Polished Shabad stone flooring | Polished Shabad stone flooring | As per relevent standard specification | 730 | M2 | 29200
38 | 5.3 | Skirting with polished shabads stone quality and approved size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and pointing with cement, labour etc, complete | Polished Shabad stone Skirting | Polished Shabad stone Skirting | As per relevent standard specification | 808 | M2 | 4282.4
39 | 106 | Painting in all floors as specified with two coats of Plastic emulation paint of approved colour make and shade over one coat of white primer including cost and conveyance of all materials, labour charges at all leads, lifts, hights, levels and floors,all incidental charges etc. complete for finished item of work . | Plastic emulsion | Plastic emulsion | As per relevent standard specification | 155 | M2 | 16430
40 | 1344 | Painting to External Faces of walls(outside) in all floors as specified with two coats of ACE or equivalent quality paint of approved colour make and shade over one coat of white cement primer including cost and conveyance of all materials, labour charges at all leads, lifts, hights, levels and floors,all incidental charges etc. complete for finished item of work . | ACE painting | ACE painting | As per relevent standard specification | 259 | Sqm | 348096
41 | 13 | Providing and applying Surya Cem of three coats of approved brand and shade to give an even shade after thoroughly brushing the surface to remove all dirt and remains of loose powdered materials, including cost and conveyance of all materials to work site and all operational, incidental, labour charges etc. complete for finished item of work | Surya cem 3coats | Surya cem 3coats | As per relevent standard specification | 85 | M2 | 1105
42 | 2 | Conducting of DGPS & Total Staion Survey and Providing of maps including preparation of boundary and contour levels with 2 Nos hard copies and soft copies complete for finished items of work as directed by the Engineer in charge of the work. | Total Station Survey | Total Station Survey | As per relevent standard specification | 5000 | EA | 10000
43 | 54.5 | Supply&Spreading ofHBG metal 20 mm size of 80mm thick including cost&conveyance labour charges etc complete for finished item of work | 20mm HBG metal | 20mm HBG metal | As per relevent standard specification | 1672 | Cum | 91124
44 | 114 | Supply&Fabrication and fixing of Welded wire mesh ( 2" x 1") of 2.8mm dia. with ISMC (75x40x4.4mm) and Pheriperal frame of ISA(35x35x3mm) including cost& conveyance painting with synthetic enamil paint two coats over a coat of red oxide primer etc complete for finished item of work. | MS Security fencing | MS Security fencing | As per relevent standard specification | 2310 | Sqm | 263340
45 | 18.15 | Supply and Fixing of MS Gates of approved design including cost and conveyance of all materials fabrication charges etc Complete for finished item of work | S&F of MS Gate | S&F of MS Gate | As per relevent standard specification | 5299 | Sqm | 96176.85
46 | 7.5 | Supply&Fixing of R.C.C hume pipe of 450 mm dia including cost & conveyance of all materials labour charges etc complete for finished item of work. | RCC hume pipes | RCC hume pipes | As per relevent standard specification | 1474 | Rmt | 11055
47 | 40 | Supply and fixing 25mm dia 1.5mm thick recessed( concealed) PVC pipe alog with reinforcement to be laid in slab including No 14 SWG GI wire for earth contunity, cost of pipe, binding wire and all labour charges etc complete, Electrical Items | concealed PVC casing | concealed PVC casing | As per relevent standard specification | 97 | M | 3880
48 | 30 | Supplying and fixing of 25mm dia 1.5mm thick PVC conduit pipe conceald in wall with all required accessories with No 14 SWG wire for earth conitunity including chisiling the wall whereever necessary, including masonary work and all labour charges complete. | concealed PVC casing | concealed PVC casing | As per relevent standard specification | 108 | M | 3240
49 | 15 | Wiring with 2X1.0 Sqm(14/.3mm) PVC insulated flexiable copper cable in the existing metalic/Non metalic conduit pipe with 6A modular SP switch, mounted on metalic box covereds with appropriate front plate modules etc ceiling rose including cot and conveyance of all mateials, labour charges complete for light points, bell points exhaust fan points in non residential builsing except circuit moving finished in all types masonary as directed by department (Anchor Roma/GM/HAVELLS/ FINOLEX) | light points | light points | As per relevent standard specification | 642 | EA | 9630
50 | 6 | Supplying and erection of approved make 6 Amps one modular SP switch with 6 Amps 6 pin mudular type plug socket mounted on metallic box covered with appropriate front plate as including all labour and material charges etc., complete for finished item of work. | 6 A sockets | 6 A sockets | As per relevent standard specification | 542 | EA | 3252
51 | 30 | supplying and run of 2 of 14/0.3 mm(1.0 sqmm) PVC insulated flexiable copper cable in existing conduit pipe for run of mains including all labour charges and materials chages etc. complete. (FINOLEX/HAVELS) | 1.0 sqmm wiring | 1.0 sqmm wiring | As per relevent standard specification | 56 | M | 1680
52 | 120 | supplying and run of 2 of 28/0.3 mm(2.5 sqmm) PVC insulated flexiable copper cable in existing conduit pipe for run of mains including all labour charges and materials chages etc. complete. (FINOLEX/HAVELS) | 2.5 sqmm wiring | 2.5 sqmm wiring | As per relevent standard specification | 103 | M | 12360
53 | 1 | Supply and fixing of 12 way SPN Distribution board with IP-20 protection suitable for single phase 40A DP Isolator/ELCB/RCCB as incomer and 10kA-6-32A SP MCBs 6Nos as out going including connections and all labour charges concealed in wall by chiseling and masonaqry work etc complete. | 12 way SPN Distribution | 12 way SPN Distribution | As per relevent standard specification | 6394 | EA | 6394
54 | 8 | Supply and erecting of approved make crom/bajaj make as directed by department 1x40W patty type fluorscent fitting made of CRCA sheet,completed with polyster filled 40W.choke,starter and side holders etc.complete with 40W tube all lobour charges etc complete (PHILIPS/CROMPTON) | tube lights | tube lights | As per relevent standard specification | 755 | EA | 6040
55 | 4 | Supply and fixing of batten holder/slanting holder in lieu of ceiling rose of light point complete with all connections and all labour charges with 11 to CF2 etc complete.(PHILIPS/CROMPTON) | batten holder | batten holder | As per relevent standard specification | 141 | EA | 564
56 | 2 | Supply and errection ceiling fan of selected colour and delux model high breeze with 3 blades and double ball bearing and with condenser AC 250 V 50 C/S of 48" 600 mm sweep completed erected in position with resistance type regulator, canopy down rod upto 304.8 mm in length is provided with hook/clamps nuts and bolts and 24/0.2 flexible copper wire etc.,complete and pointed with lettering by enamel paint the Sr.No and date of erection including cost and conveyance of all labour charges (Almonard/CG/Khaitan/Bajaj) and as per the direction of Engineer in charge. | ceiling fan | ceiling fan | As per relevent standard specification | 2277 | EA | 4554
57 | 2 | Supply and fixing of Electronic Regulator of Modular of GM / Legrand Myrius / L & T / North West / Indo Simon / ABB /Schneider ZEN celo including cost and conveyance of all labour charges and as per the direction of Engineer in charge. | Regulator for ceiling fan | Regulator for ceiling fan | As per relevent standard specification | 589 | EA | 1178
58 | 1 | Providing independent earthing for sophisticated equipment like computer, medical equipment electronic gadgets etc with 600X600X3.15mm thick copper plate rigidly fixed to the 40mm dia GI pipe 2.5m long pipe and 19mm dia B class GI pipe of .3 mts long connectd with reducer providing of stggred holes of 16 Nos of 12 mm dia to earth electrode, enclosed in in a CC chamber of (400X400X400) mm with suitable reinforced RCC slab cover duly filling with betonite powder and clay in (1:6) prop from bottom of pipe to bottom of CC chamber giving earth connection from the electrode throuh necessary GI strip of 25X6X200 mm length provided with suitable size o 14 Nos holes GI washers nuts and bolts and all labour charges etc complete. | earthing | earthing | As per relevent standard specification | 5345 | EA | 5345
59 | 40 | a)15.90mm OD Pipe - SDR 11, Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007), Water supply and sanitary items | 15.90mm OD CPVC pipes & fittings | 15.90mm OD CPVC pipes & fittings | As per relevent standard specification | 239 | M | 9560
60 | 80 | b) 22.20mm OD Pipe - SDR 11 | 22.20mm OD CPVC pipes & fittings | 22.20mm OD CPVC pipes & fittings | As per relevent standard specification | 313 | M | 25040
61 | 90 | c) 28.60mm OD Pipe - SDR 11 | 28.60mm OD CPVC pipes & fittings | 28.60mm OD CPVC pipes & fittings | As per relevent standard specification | 410 | M | 36900
62 | 20 | a) 20 mm NB Size, S & F Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type | 20mm Ball valve | 20mm Ball valve | As per relevent standard specification | 331 | EA | 6620
63 | 2 | b) 25 mm NB Size | 25mm Ball valve | 25mm Ball valve | As per relevent standard specification | 466 | EA | 932
64 | 20 | Supply and Fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand including cost and conveyance, labour charges of all materials etc. complete for finished item of work. | 110mm PVC/SWR pipe | 110mm PVC/SWR pipe | As per relevent standard specification | 462 | M | 9240
65 | 2 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) including cost and conveyance, labour charges of all materials etc. complete for finished item of work. | 110mm PVC/SWR Plain bend | 110mm PVC/SWR Plain bend | As per relevent standard specification | 96 | EA | 192
66 | 2 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) including cost and conveyance, labour charges of all materials etc. complete for finished item of work. | 110mm PVC/SWR door bend | 110mm PVC/SWR door bend | As per relevent standard specification | 128 | EA | 256
67 | 2 | Supply & fixing of Floor Trap (Bell Mouth ) 110 mm - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) including cost and conveyance, labour charges of all materials etc. complete for finished item of work. | 110mm PVC/SWR floor trap | 110mm PVC/SWR floor trap | As per relevent standard specification | 269 | EA | 538
68 | 2 | Supply&fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) including cost and conveyance, labour charges of all materials etc. complete for finished item of work. | 4" Nahany trap | 4" Nahany trap | As per relevent standard specification | 134 | EA | 268
69 | 1 | Constructing 457.2 mm x 457.2 mm (1'6"x1'6") brick in CM 1:6 prop. Masonry. Inspection chamber up to 914.4 mm (3'0") and fitted with light weight 457.2 mm x 457.2 mm (1'6"x1'6") C.I frame and cover of 20 Kg. | (1'6"x1'6") brick inspection chamber | (1'6"x1'6") brick inspection chamber | As per relevent standard specification | 4610 | EA | 4610
70 | 1 | Supplying and Fixing European Water Closet of 1st quality conforming to IS:2556-Part-2-1973 of Hindustan / Neycer or Parryware make white glazed with 'S' trap including cost and conveyance, labour charges etc complete. | European Water Closet | European Water Closet | As per relevent standard specification | 2228 | EA | 2228
71 | 2 | Supplying and fixing of best indian make plastic seat and lid for European water closets and buffers as per IS 2548-1963 | plastic seat and lid for EWC | plastic seat and lid for EWC | As per relevent standard specification | 1324 | EA | 2648
72 | 2 | Supply and fixing of PVC low level system parryware/slim line with internal component and short bend of 10 lits capacity with choice color etc., complete. | PVC low level tank | PVC low level tank | As per relevent standard specification | 2032 | EA | 4064
73 | 2 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Hand wash basin | Hand wash basin | As per relevent standard specification | 1717 | EA | 3434
74 | 2 | Suplying and fixing of angle stop cock 12.7mm dia fisrt quality indian make seiko or equivalent. | 12.7mm stop cock | 12.7mm stop cock | As per relevent standard specification | 721 | EA | 1442
75 | 2 | Suplying and fixing of bib tap 12.7mm dia fisrt quality indian make seiko or equivalent. | 12.7mm bib tap | 12.7mm bib tap | As per relevent standard specification | 298 | EA | 596
76 | 1000 | Providing and placing on terrace (at all floor levels) Sintex /Aqua tech or equivalent Polyethylene water storage tank double layer conforming to ISI 12701/96 mark with lid and suitable locking arraqngments and making necessary holes for inlet and outleta and over flow pipes labour charges etc complete for finished item of work. | PVC Sintex tank | PVC Sintex tank | As per relevent standard specification | 10 | L | 10000
77 | 1 | Suplying and fixing of 31.75mm PVC waste pipe for wash basin including cost and conveyance of all materials and labour charges et complete | PVC waste pipe | PVC waste pipe | As per relevent standard specification | 33 | EA | 33
78 | 1 | Supplying and fixing of TV shape mirror with plastic size 609mmX 457.2 m | TV shape mirror | TV shape mirror | As per relevent standard specification | 564 | EA | 564
79 | 1 | Constructing 1220.0 mm (4’0”) dia Septic tank with CC collars/rings including excavating pit up to a depth of 1800 mm (6'-0") in all sorts of soils (excluding rock), laying cement concrete (1:4:8) 150 mm thick using 40mm HBG Metal, Plastering 20mm thick for jointing CC collars and Providing M-20(Nominal mix) grade 3" thick RCC cover and including cost and conveyance of all materials like cement, sand, bricks, water etc., to site and all incidental and operational, labour charges etc., complete for finished item of work as directed by the Engineer in charge. | 4’0” dia Septic tank | 4’0” dia Septic tank | As per relevent standard specification | 8215 | EA | 8215
80 | 1 | Constructing 1220.0 mm (4’0”) dia Soak pit with reinforced brick masonary(honey-comb wall) including excavating pits up to a depth of 1500 mm (5'-0") in all sorts of soils (excluding rock) as per Standard specification and including cost and conveyance of all materials like cement, sand, bricks, water etc., to site and all incidental and operational, labour charges etc., complete for finished item of work as as directed by the Engineer in charge. | 4’0” dia Soak pit | 4’0” dia Soak pit | As per relevent standard specification | 5560 | EA | 5560
81 | 1 | Supply of steel table of size 4'x2.'x30" with 18 mm plywood fixed with rubber beeding with drawers on right side with automatic locking arrangements etc copmlete, Furniture and name boards | steel table | steel table | As per relevent standard specification | 7800 | Each | 7800
82 | 2 | supply of 'S' type chair with arms teakwood frame with seat back 's' type on G.I pipe.(Make: Godraj) | S type chairs | S type chairs | As per relevent standard specification | 3650 | Each | 7300
83 | 2 | Supply of P V C chairs of approved quality & make incldg cost etc complete | PVC Chairs | PVC Chairs | As per relevent standard specification | 1150 | Each | 2300
84 | 15 | S&F ACP Vinyl Sign Board with MS Frame | Name boards | Name boards | As per relevent standard specification | 584 | FT2 | 8760
85 | 1.62 | Supply and Fixing of Substation name board of size 6'x3' iron sheet with angle frame and channel supports of size 75x40mm, 8' height including concreting of channel supports and painting with enamel paint complete. | Name boards | Name boards | As per relevent standard specification | 4326 | Sqm | 7008.12
86 | 73.31 | Seigniorage Charges - Sand | Seigniorage Charges | Seigniorage Charges |  | 40 | M3 | 2932.4
87 | 73.31 | Seigniorage Charges -M Sand | Seigniorage Charges | Seigniorage Charges |  | 97.5 | M4 | 7147.73
88 | 390.43 | Seigniorage Charges - Metal | Seigniorage Charges | Seigniorage Charges |  | 97.5 | M3 | 38066.925
89 | 744 | Seigniorage Charges - Garvel | Seigniorage Charges | Seigniorage Charges |  | 30 | M3 | 22320
90 | 47 | Excavation of pits in hard rock not requiring blasting (In hard murram / rock boulders) for 11mtr PSCC Poles 0.75 M x 0.9 M x 1.95 M | Civil work | Exc of Hard pit w/o blast 0.75 M x 0.9 M x 1.95 M | As per relevent standard specification | 991 | EA | 46577
91 | 10 | Excavation of pits in hard rock not requiring blasting (In hard murram/rock boulders) fo 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Civil work | Exca Hard pit w/o blast 0.76X0.76X1.83M | As per relevent standard specification | 928 | EA | 9280
92 | 10 | Erection of 9.1 M long PSCC pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation: | Erection work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 24000
93 | 5.4 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.:Including the cost of cement | Civil Work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 35526.6
94 | 47 | Erection of 11mtr PSCC poles in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation: | Erection work | Erection of 11mtr PSCC poles | As per relevent standard specification | 4337 | EA | 203839
95 | 27.9 | 33/11KV Sub-Station Fabrication & erection of Channels:Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Fabrication work | Fabrication of struc.with power drilling | As per relevent standard specification | 6852 | TO | 191170.8
96 | 31 | 33/11KV Sub-Station Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.:Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Supply Material | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 67611
97 | 47.25 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.:Including the cost of cement | Civil Work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 310857.75
98 | 47 | 33/11KV Sub-Station Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.:Painting of all suppports to a height of 0.3m coping with bituminous paint (black colour) and painting of coping with two coats of white cement (including cost of paint) | Supply Material | Painting of supports to a height of 0.3M | As per relevent standard specification | 686 | EA | 32242
99 | 31 | 33/11KV Sub-Station Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*) Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work:(*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Supply Material | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 40083
100 | 31 | 33/11KV Sub-Station Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*) Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work:(*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Supply Material | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 14942
101 | 6 | 33/11KV Sub-Station Bus Stringing:Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 4.5mt) | Electrical work | Hoisting post ins&hrd wr 1panther 33kv | As per relevent standard specification | 781 | EA | 4686
102 | 2 | 33/11KV Sub-Station Bus Stringing:Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Electrical work | Hoisting post ins&hrd wr 1panther 11kv | As per relevent standard specification | 507 | EA | 1014
103 | 65 | 33/11KV Sub-Station Bus Stringing:Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Electrical work | Conn. of equip/bus single zebra/panther | As per relevent standard specification | 224 | EA | 14560
104 | 45 | 33/11KV Sub-Station Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961):Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . | Supply Material | Sup T clamp LM6 Al alloy of 12 mm, 800 A | As per relevent standard specification | 299 | EA | 13455
105 | 18 | 33/11KV Sub-Station Bus Stringing:Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. | Electrical work | S-Tension HW 3Bolt 1Zebra/Pnthr 150mm | As per relevent standard specification | 2055 | SET | 36990
106 | 12 | 33/11KV Sub-Station Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961):Supply of Bimetalic Copper die clamps suitable for power transformer/ Lclamps HV of 1/2 inch bush rod and other end suitable for panther conductor and with bimetallic sheet on the pad of size 75X75X10mm with four holes of 14mm diameter (hole to hole distance 40mm) with suitable GI bolts and nuts including washers | Supply Material | Sup Bimetalic Copper die clamps for PTR | As per relevent standard specification | 909 | EA | 10908
107 | 6 | 33/11KV Sub-Station Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961):Supply of Alluminum Post type insulator suupport clamps conforming to A6 of IS 617, with hot dip galvanised bolts and nuts suitable for 11 kV | Supply Material | SupPost type insulator suupp clamps 11kV | As per relevent standard specification | 381 | EA | 2286
108 | 12 | 33/11KV Sub-Station Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961):Supply of I Bolts | Supply Material | Supply of I-Bolts | As per relevent standard specification | 294 | EA | 3528
109 | 12 | 33/11KV Sub-Station Fixing of clamps :I - bolts | Electrical work | Fixing of I-bolts | As per relevent standard specification | 20 | EA | 240
110 | 33 | 33/11KV Sub-Station Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961):Supply of CT stud clamps with hot dip galvanised bolts and nuts suitable for zebra / Panther conductor on one side and 28/30/40 mm CT stud on other side with stud size for single zebra / panther (4 bolted) with bimetallic sleeve for carrying 800 A | Supply Material | Sup CT stud clamps 1Zebra/Panth for 800A | As per relevent standard specification | 399 | EA | 13167
111 | 54 | 33/11KV Sub-Station Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961):Supply of Alluminum alloy Pad clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR/Zebra of pad size 100 X 100 X 15mm for carrying 600 A current rating . | Supply Material | SupPad clamps 100X100X15 mm 1 panth 600A | As per relevent standard specification | 264 | EA | 14256
112 | 33 | 33/11KV Sub-Station Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961):Supply of Alluminum LA clamps conforming to A6 of IS 617, with hot dip galvanised bolts and nuts suitable for single zebra / Panther | Supply Material | Sup LA clamps for single zebra / Panther | As per relevent standard specification | 357 | EA | 11781
113 | 75 | Dismantling of Equipment :Labour for Fixing of all types of clamps | Electrical work | Labour for Fixing of all types of clamps | As per relevent standard specification | 65 | EA | 4875
114 | 8 | Erection of AB Switch and aligment complete:Erection of 33 KV AB Switch including alignment and earthing | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 36000
115 | 19 | Erection of AB Switch and aligment complete:Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 60800
116 | 25 | 33/11KV Sub-Station Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.:Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Supply Material | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 3550
117 | 63.76 | 33/11KV Sub-Station Supply of HBG metal:Excavate-Pit for 33KV VCB |  | Excavate-Pit for 33KV VCB | As per relevent standard specification | 331 | M3 | 21104.56
118 | 67 | 33/11KV Sub-Station Supply of HBG metal:Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | Supply Material | Cement concrete with 40MM metal VCB plin | As per relevent standard specification | 5160 | M3 | 345720
119 | 8 | 33/11KV Sub-Station Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc:Erection of 11 KV VCB with Control Panel | Electrical work | Erection of 11kv VCB | As per relevent standard specification | 12000 | EA | 96000
120 | 3 | 33/11KV Sub-Station Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc:Erection of 33 KV VCB with Control Panel | Electrical work | Erection of 33kv VCB | As per relevent standard specification | 12500 | EA | 37500
121 | 1 | 33/11KV Sub-Station Control panels:Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. | Supply Material | Supply of AC Supply panel complete | As per relevent standard specification | 42000 | EA | 42000
122 | 1 | 33/11KV Sub-Station Supply of HBG metal:Fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supply | Electrical work | 33/11kv S.S Erection of AC&DC Panel | As per relevent standard specification | 7871.85 | SET | 7871.85
123 | 1 | Loading of 220 V Batterry with charger | Civil Work | Loading 220 V Battery with Charger | As per relevent standard specification | 1612 | SET | 1612
124 | 1 | Un loading of 220 V Batterry with charger | Civil Work | Un-loading 220 V Battery with Charger | As per relevent standard specification | 1024 | SET | 1024
125 | 1 | 33/11KV Sub-Station Supply of HBG metal:Erect-220V Batery with Chrgr incl all-SS | Electrical work | Erect-220V Batery with Chrgr incl all-SS | As per relevent standard specification | 6442.58 | EA | 6442.58
126 | 2 | 33/11KV Sub-Station Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc:Erection of 11 KV three phase PTs | Electrical work | Erection of 11kv three phase PT s | As per relevent standard specification | 800 | SET | 1600
127 | 2 | 33/11KV Sub-Station Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc:Erection of 33 KV LAS station/Line type including earthing | Electrical work | Erect of 33kv LA stn type incl earthing | As per relevent standard specification | 880 | SET | 1760
128 | 2 | 33/11KV Sub-Station Supply of HBG metal:Erection of 33kv LA-3Nos Line type | Electrical work | Erection of 33kv LA-3Nos Line type | As per relevent standard specification | 880 | SET | 1760
129 | 2 | 33/11KV Sub-Station Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc:Erection of 11 KV LAS station type including earthing | Electrical work | Erect of 11kv LA stn type incl earthing | As per relevent standard specification | 559 | SET | 1118
130 | 32 | Providing of Earthing:Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Electrical work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 39494.4
131 | 32 | Providing of RCC collar to earth pit.:Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Civil Work | ERECT. OF LINES-Providing of RCC collar | As per relevent standard specification | 386 | EA | 12352
132 | 800 | 33/11KV Sub-Station Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication.:75x 8mm MS Flat / GI Flat. | Electrical work | Laying of earth mat,excavation 75x 8mm | As per relevent standard specification | 65 | RMT | 52000
133 | 1200 | 33/11KV Sub-Station Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc.:M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Electrical work | Earthing for raisers of SS Flat 50x6 mm. | As per relevent standard specification | 41 | RMT | 49200
134 | 440 | 33/11KV Sub-Station Control panels:Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Electrical work | Lay-Cable Terminations to Switchgear | As per relevent standard specification | 34.43 | EA | 15149.2
135 | 14 | 33/11KV Sub-Station Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE / CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA/OSRAM/SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty:i. 90W LED Fixture set | Supply Material | S-90W LED fixture set | As per relevent standard specification | 8200 | EA | 114800
136 | 14 | 33/11KV Sub-Station Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE / CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA/OSRAM/SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty:Supply and Fixing of junction box and Providing with proper Fuse protection and required glauds suitable for Cable Terminations. The box shall be fixed on the pole. | Electrical work | 33/11kv S.S Yard lighting junction box | As per relevent standard specification | 351.9 | EA | 4926.6
137 | 3000 | 33/11KV Sub-Station Control Cable:Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Electrical work | Lay-4C/10C 2.5Sqmm Control Cable | As per relevent standard specification | 27 | M | 81000
138 | 3 | 33/11KV Sub-Station Marshalling Box:Supply of MS Powder coted PT Marshalling Box | Supply Material | Sup of MSPowder coted PT Marshalling Box | As per relevent standard specification | 4095 | EA | 12285
139 | 12 | 33/11KV Sub-Station T&P:LC Boards | Supply Material | Supply of LC Boards | As per relevent standard specification | 116 | EA | 1392
140 | 24 | 33/11KV Sub-Station T&P:Danger boards with clamps | Supply Material | Supply of Danger boards with clamps | As per relevent standard specification | 116 | EA | 2784
141 | 12 | 33/11KV Sub-Station T&P:Painting of Name Plates for any equipment | Civil Work | Painting of Name Plates for any equipmen | As per relevent standard specification | 122 | EA | 1464
142 | 500 | 33/11KV Sub-Station Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961):Supply of Hot dip galvanized/zinc coated bolts & nuts including spring washers, pack washers and flat washers etc. | Supply Material | S-Hot dip gal./Zinc bolts & nuts washer | As per relevent standard specification | 90 | KG | 45000
143 | 7 | Loading of 11 KV VCBs along with Panel boards | Civil Work | LOADING of 11 KV VCBs&Panel boards | As per relevent standard specification | 1024 | EA | 7168
144 | 3 | Loading of 33 KV VCBs along with Panel boards | Civil Work | LOADING of 33 KV VCBs&Panel boards | As per relevent standard specification | 1024 | EA | 3072
145 | 3 | Un loading of 33 KV VCBs along with Panel boards | Civil Work | UNLOADING of 33 KV VCBs&Panel boards | As per relevent standard specification | 1044.48 | EA | 3133.44
146 | 7 | Un loading of 11 KV VCBs along with Panel boards | Civil Work | UNLOADING of 11 KV VCBs&Panel boards | As per relevent standard specification | 1044.48 | EA | 7311.36
147 | 3 | 33/11KV Sub-Station Marshalling Box:Erection of Marshalling boxes | Erection work | Erection of Marshalling boxes | As per relevent standard specification | 374.85 | EA | 1124.55
148 | 1 | 33/11KV Sub-Station Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc:Erection of 33 KV single phase PTs | Electrical work | Erection of 33kv single phase PT s | As per relevent standard specification | 1079 | SET | 1079
149 | 2 | 33/11KV Sub-Station Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc:Erection of 11 KV three phase PTs | Electrical work | Erection of 11kv three phase PT s | As per relevent standard specification | 800 | SET | 1600
150 | 34.7 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries (excluding of loading & unloading ) above 10 KM and upto 20 KM | Transportation | TRANSPORT OF STEEL 10 TO 20KM | As per relevent standard specification | 412.08 | TO | 14299.176
151 | 34.7 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Civil Work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 7668.7
152 | 34.7 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Civil Work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 6419.5
153 | 18 | Loading of 11KV AB Switch Conventional type | Civil Work | LOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 1440
154 | 8 | Loading of 33KV 800 Amps AB Switch | Civil Work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 1008
155 | 6 | Loading of 11 KV, 10 KA LAs Station type | Civil Work | LOADING of 11 KV,10 KA LAs Station type | As per relevent standard specification | 32 | EA | 192
156 | 9 | Loading of 33 KV, 10 KA LAs Station type | Civil Work | LOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 41 | EA | 369
157 | 6 | Un loading of 11 KV, 10 KA LAs Station type | Civil Work | UNLOADING of 11 KV,10 KA LAs Station typ | As per relevent standard specification | 32 | EA | 192
158 | 9 | Un loading of 33 KV, 10 KA LAs Station type | Civil Work | UNLOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 35 | EA | 315
159 | 3000 | Loading of PVC Control Cable 10 Core | Civil Work | Load-PVC Control Cable 10C | As per relevent standard specification | 1 | M | 3000
160 | 3000 | Un loading of PVC Control Cable 10 Core | Civil Work | UnLoad-PVC Control Cable 10C | As per relevent standard specification | 1.02 | M | 3060
161 | 15 | Un loading of 11KV AB Switch Conventional type | Civil Work | UNLOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 1200
162 | 8 | Un loading of 33KV 800 Amps AB Switch | Civil Work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 632
163 | 3 | RMUs:Supply Neutral link for PT Marshalling Box for indoor SS | Supply Material | S-Neutral Link for PT Marshl Box | As per relevent standard specification | 385 | EA | 1155
164 | 2 | TRE: :Earthing of arrangement labour for PTR Neutral | Electrical work | Earthing arangemnt labour for PTRNeutral | As per relevent standard specification | 838 | EA | 1676
165 | 4 | S&F-Nylon Neutral Link Base | Supply Material | S&F-Nylon Neutral Link Base | As per relevent standard specification | 106.25 | EA | 425
166 | 10 | Sub-transport of 9.1 Mtrs long PSCC Poles upto Workspot upto 10KM (Including loading and unloading) | Civil Work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 4072.9
167 | 36 | Un loading of 33 & 11 KV Disc insulators | Civil Work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | KI | 72
168 | 2 | Loading of 33 KV Metal parts | Civil Work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 130
169 | 2 | Un loading of 11 KV Metal parts | Civil Work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 96
170 | 2 | 33/11KV Sub-Station Erection of PTR on constructed plinth :Erection of 8 MVA PTR. | Electrical work | Erec 33/11 KV, 8 MVA PTR as per Spec | As per relevent standard specification | 49480.2 | EA | 98960.4
171 | 14 | 33/11KV Sub-Station Yard lightning:Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. | Supply Material | Supply 9mtrs tubular poles single way | As per relevent standard specification | 13913 | EA | 194782
172 | 14 | 33/11KV Sub-Station:Erection of tubular poles | Erection work | Errection of tubular poles | As per relevent standard specification | 1379 | EA | 19306
173 | 14 | 33/11KV Sub-Station Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE / CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA/OSRAM/SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty:Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. | Electrical work | Fixing of LED/Metal halide complete. | As per relevent standard specification | 1268 | EA | 17752
174 | 27.9 | 33/11KV Sub-Station Fabrication & erection of Channels:Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Fabrication work | Alligning the Main/Aux. structures. | As per relevent standard specification | 1470 | TO | 41013
175 | 500 | 33/11KV Sub-Station Control panels:Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions | Electrical work | Supply,fabricati of 6mm Checkerd plates | As per relevent standard specification | 83 | KG | 41500
176 | 8 | 33/11KV Sub-Station Bus Stringing:Supply of Tension clamps for earth wire 3 bolted. | Supply Material | SupTension clamps for earthwire 3bolted | As per relevent standard specification | 715 | SET | 5720
177 | 31 | 33/11KV Sub-Station Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961):Supply of Alluminum alloy Pad clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for twin panther ACSR/Zebra of pad size 100 X 100 X 15mm for carrying 1200 A current rating . | Supply Material | SupPad clamps 100X100X15mm 2 panth 1200A | As per relevent standard specification | 284 | EA | 8804
178 | 12 | 33/11KV Sub-Station Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961):Supply of Alluminum PT clamps conforming to A6 of IS 617, with hot dip galvanised bolts and nuts suitable for single zebra / Panther | Supply Material | Sup PT clamps for single zebra / Panther | As per relevent standard specification | 368 | EA | 4416
179 | 200 | 33/11KV Sub-Station Bus Stringing:Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | Electrical work | Stringing of bus with panther conductor | As per relevent standard specification | 327.68 | M | 65536
180 | 1 | 33/11KV Sub-Station Control panels:Erection of control/Relay panels, AC Panels, announciation panels etc in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Electrical work | Erect-Contrl/Relay, AC, Announ. Panels | As per relevent standard specification | 2122 | EA | 2122
181 | 21.6 | Earth work excavtion hard rock boulders not requiring blasting.(In hard murram / rock boulders) (other than SS) | Electrical work | Earth work excav hard rock bould <3cum | As per relevent standard specification | 1318.35 | M3 | 28476.36
182 | 4 | 33/11KV Sub-Station :Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. | Supply Material | SupCU Flexi jumper for Power T/F Neutral | As per relevent standard specification | 4725 | EA | 18900
183 | 8 | 33/11KV Sub-Station Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc:Erection of 11 KV LAS line type including earthing | Electrical work | Erect of 11kvLA line type incl earthing | As per relevent standard specification | 505 | SET | 4040
184 | 32 | Supply of earthing pipe with materials :Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Supply Material | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 111552
185 | 32 | Loading of CI earth pipe 100 mm dia, 2.75 mt long | Civil Work | LOADING of CI Earth pipe upto 2.7 Mtr | As per relevent standard specification | 29 | EA | 928
186 | 32 | Un loading of CI earth pipe 100 mm dia, 2.75 mt long | Civil Work | UNLOADING of CI Earth pipe upto 2.7 Mtr | As per relevent standard specification | 29 | EA | 928
187 | 270 | 33/11KV Sub-Station Supply of HBG metal:Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Electrical work | L-Cable Termination to Switchgear | As per relevent standard specification | 27 | EA | 7290
188 | 90 | 33/11KV Sub-Station Supply of HBG metal:Providing of control cable trench as per DATA-XII | Erection work | Providing of cable trench as per DATA-IX | As per relevent standard specification | 3148 | RMT | 283320
189 | 1 | Construction of DTR Plinth:RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | Civil Work | Column type DTR Plinth topslab 4'x4'x6" | As per relevent standard specification | 25967.57 | EA | 25967.57
190 | 1 | Loading of 50,63, 75 & 100 KVA DTR | Civil Work | LOADING of 50,63,75&100kva DTR | As per relevent standard specification | 350 | EA | 350
191 | 1 | Un loading of 50,63, 75 & 100 KVA DTR | Civil Work | UNLOADING of 50,63,75&100kva DTR | As per relevent standard specification | 280 | EA | 280
192 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc:Erection of 3 Ph DTRs upto 25KVA | Erection work | Erection of Three Phase DTRs | As per relevent standard specification | 1139.95 | EA | 1139.95
193 | 30 | Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road:11KV 3x185 Sqmm Cable | Electrical work | Lay-SR 11KV 3x185sqmm UG Cb HG/BC/CC/BT | As per relevent standard specification | 465.46 | M | 13963.8
194 | 20 | Excavation & laying of 11 KV 3x185 Sqmm UG Cable in Single Runincluding excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) : | Electrical work | Raise-SR 11KV 3x185sqmm UG Cb on support | As per relevent standard specification | 126.23 | M | 2524.6
195 | 2 | UG Cables Joints : Making of Outdoor/Indoor End Termination:Making 11 KV 3x185 Sqmm Cable Out Door/Indoor end termination | Electrical work | OD/Idoor end termination 11kv 3x185 xlpe | As per relevent standard specification | 2370.63 | EA | 4741.26
196 | 1 | Erection of AB Switch and aligment complete:Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | Electrical work | Erection of LT distribution box | As per relevent standard specification | 1594.67 | EA | 1594.67
197 | 1 | 33/11KV Sub-Station Control panels:Supply of DC Annunciation & relay panel for 10 feeder panel including the cost of LED Indiacation lamps, VAA auxilairy relays, Electronic Hooters complete as per specification. | Supply Material | Supply of DC Anunc.relay panel 8 feeders | As per relevent standard specification | 42500 | EA | 42500
198 | 3 | 33/11KV Sub-Station Marshalling Box:Supply of FRP PT Marshalling Box | Supply Material | Supply of FRP PT Marshalling Box | As per relevent standard specification | 4463 | EA | 13389
199 | 10 | 33/11KV Sub-Station Testing of Sub-Station Equipment:Wirring, commissioning and testing of Outdoor Sub-station switchgear duly conducting the pre commissioning test as per relevent standards & issue of certificate by CEIG authorised testing Engineer | Electrical work | Testing of Outdoor SS switchgear | As per relevent standard specification | 1825 | EA | 18250
200 | 2 | 33/11KV Sub-Station Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading ) :8MVA power transformer | Transportation | Transport of 8MVA power transformer | As per relevent standard specification | 21945 | EA | 43890
201 | 2 | 33/11KV Sub-Station Loading and unloading of PTR on constructed plinth :Loading of 8MVA PTR | Civil Work | LOADING of 8 MVA PTR | As per relevent standard specification | 5805.84 | EA | 11611.68
202 | 2 | 33/11KV Sub-Station Loading and unloading of PTR on constructed plinth :Unloading of 8MVA PTR | Civil Work | UNLOADING of 8 MVA PTR | As per relevent standard specification | 5805.84 | EA | 11611.68
203 | 2 | 33/11KV Sub-Station Testing of Sub-Station Equipment:Testing of Power Transformer duly conducting the pre commissioning tests as per relevent standard & issue of certificate by CEIG authorised testing Engineer | Electrical work | Testing of Power Transformer. | As per relevent standard specification | 4000 | EA | 8000
204 | 75 | Supply of earthing pipe with materials :Supply of GI Flat 25X3 mm | Supply Material | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 7875
205 | 90 | Excavation & laying of LT 3 1/2 x 185 Sqmm Cable UG Cable in Single Run including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road: | Electrical work | Lay-SR LT 3.5x185sqmm UG Cb HG/BC/CC/BT | As per relevent standard specification | 377.63 | M | 33986.7
206 | 10 | Excavation & laying of LT 3 1/2 x 185 Sqmm UG Cable in Single Run including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) : | Electrical work | Raise-SR LT 3.5x185sqmm UG Cb on support | As per relevent standard specification | 85.43 | M | 854.3
207 | 2 | UG Cables Joints : Making of Outdoor/Indoor End Termination:Supply of 31/2x185Sqmm UG O/D end termination kits | Supply Material | Sup of 31/2x185Sqmm UG O/D end term kits | As per relevent standard specification | 550 | EA | 1100
208 | 1 | Loading of 11 KV HG Fuse Sets | Civil Work | LOADING of 11 KV HG Fuse Sets | As per relevent standard specification | 18 | EA | 18
209 | 1 | Un loading of 11 KV HG Fuse Sets | Civil Work | UNLOADING of 11 KV HG Fuse Sets | As per relevent standard specification | 18 | EA | 18
210 | 1 | 33/11KV Sub-Station Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc:Erection of 11 KV HG Fuse set including earthing | Electrical work | Erect. of 11kv HG Fuseset incl earthing | As per relevent standard specification | 740.52 | SET | 740.52
211 | 2 | UG Cables Joints : Making of Outdoor/Indoor End Termination:Supply & fixing of Oout Door/Indoor end termination LT 3 1/2 x 185 Sqmm Cable | Electrical work | OD/Idoor end termination LT 3 1/2 x 185 | As per relevent standard specification | 968.9 | EA | 1937.8
212 | 1 | Erection of AB Switch and aligment complete:Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Electrical work | Erection of 11kv TT type AB switch | As per relevent standard specification | 1813.49 | EA | 1813.49
213 | 3 | 33/11KV Sub-Station :Supply of 11kv, 200Amps copper Flexible jumpers | Supply Material | Sup11kv, 200Amps copper Flexible jumpers | As per relevent standard specification | 131 | EA | 393
214 | 1 | 33/11KV Sub-Station T&P:Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard | Electrical work | Sup &fix of board ind Switchyard layout | As per relevent standard specification | 1654 | EA | 1654
215 | 1 | 33/11KV Sub-Station T&P:Supply and fixing of safety instructions/Substation operation instruction board | Electrical work | Sup& fix safety inst/SS Op. inst board | As per relevent standard specification | 2205 | EA | 2205
216 | 1 | 33/11KV Sub-Station T&P:Wall clock standard make | Supply Material | Supply of Wall clock standard make | As per relevent standard specification | 578 | EA | 578
217 | 1 | 33/11KV Sub-Station Supply of HBG metal:S-10ft Aluminium Ladder | Supply Material | S-10ft Aluminium Ladder | As per relevent standard specification | 1654 | EA | 1654
218 | 1 | 33/11KV Sub-Station T&P:Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579-1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. | Supply Material | SupTaparia Tool kit complete as per Spec | As per relevent standard specification | 4925 | SET | 4925
219 | 1 | 33/11KV Sub-Station T&P:Rechargeable LED torch light of Standard make | Supply Material | Sup Rechargeable LED torch light. | As per relevent standard specification | 1733 | EA | 1733
220 | 1 | 33/11KV Sub-Station T&P:Steel almarah(61/2 X 3ft) Godrej | Supply Material | Sup Steel almarah(61/2 X 3ft) Godrej | As per relevent standard specification | 9818 | EA | 9818
221 | 1 | 33/11KV Sub-Station T&P:Table (3x6ft) Godrej | Supply Material | Supply of Table (3x6ft) Godrej | As per relevent standard specification | 6050 | EA | 6050
222 | 4 | 33/11KV Sub-Station T&P:S type chairs (Godrej) | Supply Material | Supply of S type chairs (Godrej) | As per relevent standard specification | 924 | EA | 3696
223 | 1 | 33/11KV Sub-Station T&P:Angle racks(18x36.6inches) Godrej | Supply Material | Sup Angle racks(18x36.6inches) Godrej | As per relevent standard specification | 1733 | EA | 1733
224 | 1 | 33/11KV Sub-Station T&P:Hack saw (12 inches) | Supply Material | Supply of Hack saw (12 inches) | As per relevent standard specification | 289 | EA | 289
225 | 4 | 33/11KV Sub-Station T&P:Earth Rods (8ft) Screw & clamp type | Supply Material | Sup Earth Rods (8ft) Screw & clamp type | As per relevent standard specification | 578 | EA | 2312
226 | 2 | 33/11KV Sub-Station T&P:Hand Gloves | Supply Material | Supply of Hand Gloves | As per relevent standard specification | 289 | SET | 578
227 | 12 | 33/11KV Sub-Station T&P:Rubber mats ( 6’x3’) size for indoor SS | Supply Material | SupRubber mats( 6’x3’)size for indoorSS | As per relevent standard specification | 1386 | EA | 16632
228 | 1 | Biometric Time attendence System & Telecom:Standard basic cell phone with charger | Supply Material | Sup Stand basic cell phone with charger | As per relevent standard specification | 1386 | EA | 1386
229 | 1 | 33/11KV Sub-Station Supply of Materials:Fire bucket stand with 3 buckets (8 -10 ltr capacity) | Supply Material | Sup Fire Buckets Stand with Buckets | As per relevent standard specification | 1386 | SET | 1386
230 | 2 | 33/11KV Sub-Station T&P:Room fire extinguisher (2 ltrs capacity) for control room | Supply Material | Sup Fire Extinguisher for Control Room | As per relevent standard specification | 4620 | EA | 9240
231 | 4 | 33/11KV Sub-Station T&P:Trolley mounted CO2 (6.5Kgs) | Supply Material | Sup TrollyMounted Co2 Cylinders(IS-2878) | As per relevent standard specification | 9240 | EA | 36960
232 | 6 | 33/11KV Sub-Station T&P:Safety Helmets of standard make | Supply Material | Supply of Safety Helmet of standard make | As per relevent standard specification | 231 | EA | 1386
233 | 4 | 33/11KV Sub-Station T&P:Gum Boots (Pair) | Supply Material | Supply of Gum Boots | As per relevent standard specification | 693 | EA | 2772
234 | 1 | 33/11KV Sub-Station T&P:5000v megger | Supply Material | Supply of 5000v megger | As per relevent standard specification | 13860 | EA | 13860
235 | 1 | 33/11KV Sub-Station T&P:Earth megger (1000v) | Supply Material | Supply of Earth megger (1000v) | As per relevent standard specification | 8085 | EA | 8085
236 | 1 | 33/11KV Sub-Station T&P:Digital clamp meter. | Supply Material | Supply of Digital clamp meter. | As per relevent standard specification | 2888 | EA | 2888
237 | 1 | 33/11KV Sub-Station T&P:Name board of the 33/11kV Sub-Station(As per Standard Specification) | Supply Material | Sup 33/11kv S.S Permanent name board | As per relevent standard specification | 10238 | EA | 10238
238 | 27.5 | 33/11KV Sub-Station Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961):Plastering 2 Coats,20/16mm(1:6)(1:4) | Civil Work | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | As per relevent standard specification | 373 | M2 | 10257.5
239 | 700 | Supply and Erection of I Hook and Suspension Hook:S/o rail poles 90/105lb (250x2N) | Supply Material | S/o rail poles 90/105lb (250x2N) | As per relevent standard specification | 47.27 | KG | 33089
240 | 4 | Erection of Rail pole 90 lbs pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation: | Erection work | Erection of Rail Pole 90Lbs | As per relevent standard specification | 3510 | EA | 14040
241 | 31 | 33/11KV Sub-Station Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.:Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Electrical work | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 26381
242 | 1 | Erection of Box pole 12 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Erection work | Erect-12Meter Box pole | As per relevent standard specification | 3901.37 | EA | 3901.37
243 | 1 | Excavation of pits in all soils except hard rock requiring blasting for 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | Civil Work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 700
244 | 9.5 | 33/11KV Sub-Station Supply of HBG metal:survey line&cabl inc peg mark&tree clear | Civil Work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 7267.5
245 | 72 | Excavation of pits in hard rock not requiring blasting (In hard murram / rock boulders) for 12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") | Civil Work | Exc.12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M(3.0" x 3.0" x 7.6") | As per relevent standard specification | 1466 | EA | 105552
246 | 10 | Excavation of pits in hard rock not requiring blasting (In hard murram/rock boulders) fo 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Civil Work | 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | As per relevent standard specification | 928 | EA | 9280
247 | 72 | Erection of Spun poles 12.5 Mtrs / 12.9Mtrs PSCC pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation: | Erection work | Errection of Spun pole12.5 mt | As per relevent standard specification | 4522 | EA | 325584
248 | 10 | Erection of 9.1 M long PSCC pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation: | Erection work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 24000
249 | 2 | Erection of Box pole 12 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Erection work | Erect-12Meter Box pole | As per relevent standard specification | 3901.37 | EA | 7802.74
250 | 2 | Fabrication of poles with 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Fabrication work | Fabrication of 175x85/150x75mm RS joist | As per relevent standard specification | 512.55 | EA | 1025.1
251 | 2 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Civil Work | Painting of RS Joist(1C RO, 2C Al.Paint) | As per relevent standard specification | 1132 | EA | 2264
252 | 88.65 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.:Including the cost of cement | Civil Work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 583228.35
253 | 2 | TOWERS:Supply of M+3 Tower (Galvanized) | Supply Material | S-M+3 Tower GALV | As per relevent standard specification | 140674.3 | EA | 281348.6
254 | 2 | TOWERS:Supply of material for Extension of 3Mtrs for M+3 (Galvanized) | Supply Material | S-Mat. for Extn of M+3 Tower by 3M GALV | As per relevent standard specification | 28520.64 | EA | 57041.28
255 | 2 | TOWERS:Erection of M+3 Tower (Galvanized) | Electrical work | Erect- M+3 Tower GALV | As per relevent standard specification | 64576 | EA | 129152
256 | 2 | TOWERS:Erection of Extension of 3Mtrs for M+3 (Galvanized) | Electrical work | Erect-Extn of 3M for M+3 Tower GALV | As per relevent standard specification | 5169 | EA | 10338
257 | 2 | TOWERS:Erection of M+3 Tower (Galvanized) | Electrical work | Erect- M+3 Tower GALV | As per relevent standard specification | 64576 | EA | 129152
258 | 2 | TOWERS:Erection of Extension of 3Mtrs for M+3 (Galvanized) | Electrical work | Erect-Extn of 3M for M+3 Tower GALV | As per relevent standard specification | 5169 | EA | 10338
259 | 9.504 | Earth work excavation of pits in hard murram/rock boulders requiring blasting (other than SS): | Civil Work | Excavate-Earth in Hard Murram | As per relevent standard specification | 1500 | M3 | 14256
260 | 20 | Formation of Cut point for 33 KV Double circuit line excluding pole erection and stays | Electrical work | Formation of 33kvline vertical cutpoint | As per relevent standard specification | 3198.72 | EA | 63974.4
261 | 3.6 | Paving out and stringing of 100 Sqmm Double Circuit (6 Conductors) conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location. : | Electrical work | Stringing 100sqmm 33/11kv Line 6 Cond DC | As per relevent standard specification | 26256 | KM | 94521.6
262 | 7.6746 | Transport of steel including line materials such as cross arms, clamps, hardware, cable (loose) and other line materials (Including loading and unloading) above 20 KM and upto 30 KM | Transportation | TRANSPORT OF STEEL MATERIAL 20 TO 30KM | As per relevent standard specification | 527.34 | TO | 4047.1278
263 | 7.6746 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Civil Work | LOADING of MS Channel,Angles, Flats&Rods | As per relevent standard specification | 221 | TO | 1696.0884
264 | 7.6746 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Civil Work | UNLOADING of MS Channel,Angles, Flats&Rod | As per relevent standard specification | 185 | TO | 1419.8025
265 | 216 | Loading of 33 KV Pin insulators | Civil Work | LOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | KI | 648
266 | 216 | Un loading of 33 KV Pin insulators | Civil Work | UNLOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | KI | 648
267 | 4.8 | Loading of 33 KV Metal parts | Civil Work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 312
268 | 6 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) above 30 Km and upto 50 Km with Lorry for each trip | Transportation | Transport of Cond Drum,VCBs >30 & <50Km | As per relevent standard specification | 4372.74 | EA | 26236.44
269 | 850 | Supply of earthing pipe with materials :Supply of GI Bolts & Nuts etc | Supply Material | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 99875
270 | 10 | Sub-transport of 9.1 Mtrs long PSCC Poles upto Workspot upto 10KM (Including loading and unloading) | Civil Work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 4072.9
271 | 72 | Sub-transport of 11/12.5/12.9M Spun polesupto Workspot upto 10KM (Including loading and unloading) | Civil Work | SubTrnsprt 12.5M Spun pole | As per relevent standard specification | 771 | EA | 55512
272 | 5 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Civil Work | Load-11/33KV XLPE UG Cable for all sizes | As per relevent standard specification | 1024 | DR | 5120
273 | 5 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Civil Work | Unload-11/33KV XLPE UG Cable all sizes | As per relevent standard specification | 1024 | DR | 5120
274 | 380 | Excavation & laying of 33 KV 3x400 Sqmm UG Cable (Triple Run ) or more Run including excavation of trench of size 1000mm wide to 750mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs Along the CC / BT multi layer road requiring compressor: | Electrical work | Lay-T.Run 33KV 3x400sqmm UG Cb | As per relevent standard specification | 1731 | M | 657780
275 | 120 | Excavation & laying of 33 KV 3x400 Sqmm UG Cable in Single Run including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) : | Electrical work | Raising 33 KV 3x400 Sqmm Cable | As per relevent standard specification | 136 | M | 16320
276 | 760 | Excavation & laying of Laying of 2nd cable in excavated trench (Six Run ) including excavation of trench of size 1050mm wide to 1200mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) | Electrical work | Lay-2nd Cable in Excavated Trench | As per relevent standard specification | 204.1 | M | 155116
277 | 380 | Supply of 6" B class GI pipe | Supply Material | S-6" B Class GI pipe 5mm thck 20Kg/M | As per relevent standard specification | 1044 | M | 396720
278 | 6 | UG Cables Joints : Making of Outdoor/Indoor End Termination:Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination | Electrical work | OD/Idoor end termination 33kv 3x400 | As per relevent standard specification | 2764.76 | EA | 16588.56
279 | 6 | UG Cables Joints : Making of Straight through joints:33 KV 3x400 Sqmm Cable | Electrical work | Straight through joint 33kv 3x400 xlpe | As per relevent standard specification | 5700.78 | EA | 34204.68
280 | 2 | Erection of AB Switch and aligment complete:Erection of 33 KV AB Switch including alignment and earthing | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 9000
281 | 2 | 33/11KV Sub-Station Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.:Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical work | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 284
283 | 10 | Excavation of pits in all soils except hard rock requiring blasting for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M (1.31 cum) | Civil Work | EXCAV. OF PIT 0.75 M x 0.9 M x 1.95 M | As per relevent standard specification | 629.85 | EA | 6298.5
284 | 8 | Loading of Conductor drums | Civil Work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 1616
285 | 5.7 | 33/11KV Sub-Station Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.:Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Supply Material | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 12431.7
286 | 5.7 | 33/11KV Sub-Station Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.:Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Civil Work | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 4850.7
287 | 5.7 | 33/11KV Sub-Station Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*) Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work:(*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Civil Work | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 7370.1
288 | 5.7 | 33/11KV Sub-Station Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*) Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work:(*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Civil Work | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 2747.4
289 | 150 | Excavation of pits in hard rock not requiring blasting (In hard murram/rock boulders) fo 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Civil Work | Exca Hard pit w/o blast 0.76X0.76X1.83M | As per relevent standard specification | 928 | EA | 139200
290 | 53 | Excavation of pits in hard rock requiring blasting (other than SS) for 9.1Mtrs PSCC Pole 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Civil Work | EXCAV. OF PIT HARD(2.6" x 2.6" x 6.0") | As per relevent standard specification | 1770 | EA | 93810
291 | 10 | Excavation of pits in all soils except hard rock requiring blasting for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M (1.31 cum) | Civil Work | EXCAV. OF PIT 0.75 M x 0.9 M x 1.95 M (1.31 cum) | As per relevent standard specification | 630 | EA | 6300
292 | 10 | Excavation of pits in hard rock not requiring blasting (In hard murram / rock boulders) for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Civil Work | EXCAV. OF PIT 0.75 M x 0.9 M x 1.95 M (1.31 cum) | As per relevent standard specification | 991 | EA | 9910
293 | 203 | Erection of 9.1 M long PSCC pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation: | Erection work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 487200
294 | 20 | Erection of 11 Mtrs PSCC poles in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation: | Erection work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4336.85 | EA | 86737
295 | 55.224 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.:Including the cost of cement | Civil Work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 363318.696
296 | 20 | Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays | Electrical work | Formatn of Horiz Cut point for 11KV line | As per relevent standard specification | 1435.81 | EA | 28716.2
297 | 5.9733 | 33/11KV Sub-Station Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.:Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Supply Material | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 13027.7193
298 | 5.9733 | 33/11KV Sub-Station Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.:Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Civil Work | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 5083.2596
299 | 5.9733 | 33/11KV Sub-Station Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*) Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work:(*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Supply Material | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 7723.4485
300 | 5.9733 | 33/11KV Sub-Station Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*) Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work:(*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Civil Work | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 2879.12
301 | 8.9 | Paving out and stringing of 55 Sqmm Single Circuit (3 Conductors)conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location. | Electrical work | Stringing of 55sqmm 33/11kv Line 3 Cond | As per relevent standard specification | 9454.81 | KM | 84147.809
302 | 203 | Sub-transport of 9.1 Mtrs long PSCC Poles upto Workspot upto 10KM (Including loading and unloading) | Civil Work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 82679.87
303 | 20 | Sub-transport of 11 Mtrs long PSCC Poles upto Workspot upto 10KM (Including loading and unloading) | Civil Work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 8639.4
304 | 4 | Erection of AB Switch and aligment complete:Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 12800
305 | 4 | 33/11KV Sub-Station Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.:Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Civil Work | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 568
306 | 80 | Supply of earthing pipe with materials :Supply of GI Flat 25X3 mm | Supply Material | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 8400
307 | 5.9733 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Civil Work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 1320.0944
308 | 5.9733 | Transport of steel including line materials such as cross arms, clamps, hardware, cable (loose) and other line materials (Including loading and unloading) above 20 KM and upto 30 KM | Transportation | TRANSPORT OF STEEL MATERIAL 20 TO 30KM | As per relevent standard specification | 527.34 | TO | 3149.9484
309 | 5.9733 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Civil Work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 1105.0564
310 | 609 | Loading of 11KV pin insulators/Post type insulators/ Solid core insulators | Civil Work | LOADING of 11kv Pin/Post/Solid Core Insu | As per relevent standard specification | 1 | KI | 609
311 | 609 | Un loading of 33 & 11 KV Disc insulators | Civil Work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | KI | 1218
312 | 8 | Loading of 11 KV Metal parts | Civil Work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 384
313 | 8 | Un loading of 11 KV Metal parts | Civil Work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 384
314 | 8 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) above 20 Km and upto 30 Km with Lorry for each trip | Transportation | Transport of Cond Drum,VCBs >20 & <30Km | As per relevent standard specification | 3691.38 | EA | 29531.04
315 | 8 | Supply of earthing pipe with materials :Supply of CI eath pipe with 50mm dia,2.0 M Length | Supply Material | S-CI Pipe earthing 50mm dia 2m long | As per relevent standard specification | 2441 | EA | 19528
316 | 8 | Providing of RCC collar to earth pit.:Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Civil Work | ERECT. OF LINES-Providing of RCC collar | As per relevent standard specification | 386 | EA | 3088
317 | 8 | Providing of Earthing:Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Electrical work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 9873.6
318 | 100 | Providing of RCC collar to earth pit.:Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete | Civil Work | Run-GI Earth Flat 25x3mm from metallic p | As per relevent standard specification | 14.03 | M | 1403
319 | 4.45 | Loading of Conductor drums | Civil Work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 898.9
320 | 4.45 | Un loading of Conductor drums | Civil Work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 445
321 | 223 | Painting of poles:Numbering of poles incl. cost of paint | Civil Work | Numbering of poles incl. cost of paint | As per relevent standard specification | 32 | EA | 7136
322 | 1115 | Supply of earthing pipe with materials :Supply of GI Bolts & Nuts etc | Supply Material | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 131012.5
[6 empty] | Tender schedule cost |  | 14411610.7713