## X-2024-12-02-03-01-001
SCHEDULE
Name of the Work :- Erection of 2 Nos. 33kV bays with 33kV bus extension at 132/33kV MD Pally outdoor EHT Sub-Station for providing of 2 Nos. new 33kV Feeders to 33/11kV CRPF Sub-station & 33/11kV Miralam Sub-Station which pertains to Lines South Division in Master Plan SD-III of Division-II in Hyderabad Circle under T&D-Master Plan Zone
WBS Element :- X-2024-12-02-03-01-001
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | Service Codes | Rate (INR) | UOM | AMOUNT
1 | 7 | Supply of 33KV TC Structure as per DATA-II | Elect | Supply | SMR40102 | 50703 | EA | 354921
2 | 2 | Supply of 33KV TD Structure as per DATA-I | Elect | Supply | SMR40101 | 20945 | EA | 41890
3 | 8 | Supply of 33KV BD Boom as per DATA-IV | Elect | Supply | SMR40104 | 18244 | EA | 145952
4 | 2 | Erection of 33KV TD Structure as per DATA-I | Elect | Labour | SWR11009 | 14839.78 | EA | 29679.56
5 | 7 | Erection of 33KV TC Structure as per DATA-II | Elect | Labour | SWR11010 | 17393.04 | EA | 121751.28
6 | 1.6 | Alligning the Main and Auxiliary structures such as RS joist,M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Elect | Labour | SWR10867 | 1470 | TO | 2352
7 | 2 | Loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10198 | 1024 | EA | 2048
8 | 1 | Transport of conductor drums, cable drums, fragilematerial such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
9 | 2 | Un loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10516 | 1044.48 | EA | 2088.96
10 | 2 | Erection of 33 KV VCB with Control Panel | Elect | Labour | SWR10460 | 12500 | EA | 25000
11 | 1.2 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Elect | Labour | SWR10206 | 221 | TO | 265.2
12 | 1.2 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Elect | Labour | SWR10524 | 185 | TO | 222
13 | 1.2 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 494.496
14 | 0.6 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 2055.6
15 | 0.6 | Alligning the Main and Auxiliary structures such as RS joist,M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Elect | Labour | SWR10867 | 1470 | TO | 882
16 | 0.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 1308.6
17 | 0.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. -Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 510.6
18 | 0.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elect | Supply | SMR40010 | 1293 | TO | 775.8
19 | 0.6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete- Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Elect | Labour | SWR10879 | 482 | TO | 289.2
20 | 2 | Erection of 33 KV CTs | Elect | Labour | SWR10399 | 1079 | SET | 2158
21 | 2 | Supply & Erection of 33KV Isolators 1200 A (ISC=31.5 KA for1Sec.) Maunal operated with all accessories, auxiliaries Marshalling boxes, terminal connectors other essentials | Elect | Supply | SWR12375 | 65800 | EA | 131600
22 | 4 | Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10239 | 126 | EA | 504
23 | 1 | Transport of conductor drums, cable drums, fragilematerial such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
24 | 4 | Un loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10557 | 79 | EA | 316
25 | 4 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 4500 | EA | 18000
26 | 6 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 852
27 | 6 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 879.78
28 | 6 | Loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10266 | 41 | EA | 246
29 | 6 | Un loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10584 | 35 | EA | 210
30 | 2 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | SET | 1760
31 | 2.52 | Supply of GI Flat 100x16mm | Elect | Supply | SMR24915 | 63235 | TO | 159352.2
32 | 200 | Laying of earth mat including excavation of trenches of depth 600mm, welding,connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the GI 100x16mm earth flat | Elect | Labour | SWR22054 | 65 | RMT | 13000
33 | 127.66 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc with MS Flat 75x8 mm. | Elect | Labour | SWR10918 | 50 | RMT | 6383
34 | 10 | Excavation of earth pit, supply of cast iron pipe with flange onone end (as per ISS7181/86) of nominal dia 125mm and 2.75meters long in side the pit including supply and fixing RCC collars 0.75 meter dia (OD), 50mm thick and 0.60meters long complete as per APTRANSCO standards | Elect | Labour | SWR10924 | 9804 | EA | 98040
35 | 1 | Loading of 11KV 3 Way RMU/Twin feeder panel | Elect | Labour | SWR10615 | 907.8 | EA | 907.8
36 | 1 | Transport of conductor drums, cable drums, fragilematerial such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
37 | 1 | Un loading of 11KV 3 Way RMU/Twin feeder panel | Elect | Labour | SWR10629 | 907.8 | EA | 907.8
38 | 1 | Erection of 33kV Twin feeder control & Relay panel in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Elect | Labour | SWR10934 | 1729 | EA | 1729
39 | 1 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 1024
40 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
41 | 1 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 1024
42 | 320 | Excavation & laying of 33kV 1Cx400 Sqmm Cu UG Cable in Single Run including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road: | Elect | Labour | SWR11926 | 387.6 | M | 124032
43 | 80 | Raising of Single run 33KV 1x400sqmm Copper UG cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11962 | 121.13 | M | 9690.4
44 | 8 | Supply of 33KV 1Cx400Sqmm O/d Cb End Kit | Elect | Supply | SMR24774 | 6792.5 | EA | 54340
45 | 8 | Installation of 33KV 1Cx400Sqmm O/d Cb End Kit | Elect | Labour | SWR24774 | 3030.5 | EA | 24244
46 | 0.24 | Supply of Moose Conductor | Elect | Supply | SMR23225 | 375155 | KM | 90037.2
47 | 1 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases withTwin Zebra/Panther conductor to a tension of 900kgs including fixing of spacer clamps.(Bus section of 4.5mt) | Elect | Labour | SWR10882 | 1302 | EA | 1302
48 | 12 | Supply of Spacer Clamp 150mm Spacing Twin Moose | Elect | Supply | SMR25240 | 294 | EA | 3528
49 | 18 | Supply of T-Clamp for Twin moose to single moose with 150 mm Spacing | Elect | Supply | SMR25242 | 694 | EA | 12492
50 | 6 | Supply of Alluminum LA clamps conforming to A6 of IS 617,with hot dip galvanised bolts and nuts suitable for single zebra / Panther | Elect | Supply | SMR40027 | 357 | EA | 2142
51 | 200 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per pecification (including cost of ferrules, lugs and glands) | Elect | Labour | SWR12510 | 27 | EA | 5400
52 | 40 | Providing of control cable trench as per DATA-XII | Elect | Labour | SWR22093 | 3148 | RMT | 125920
53 | 1800 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends | Elect | Labour | SWR11879 | 27 | M | 48600
54 | 2 | Supply of MS Powder coated CT Marshalling Box | Elect | Supply | SMR40047 | 3675 | EA | 7350
55 | 2 | Erection of Marshalling boxes | Elect | Labour | SWR10940 | 374.85 | EA | 749.7
56 | 4 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 | Elect | Supply | SMR40051 | 13913 | EA | 55652
57 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elect | Labour | SWR11039 | 928 | EA | 3712
58 | 4 | Errection of tubular poles | Elect | Labour | SWR10955 | 1379 | EA | 5516
59 | 4.23 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc | Elect | Labour | SWR10356 | 6579 | M3 | 27829.17
60 | 4 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE /CROMPTON/ BAJAJ/VIN/ WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE /NICHIA/OSRAM/ SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing,toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the roadbeam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty-90W LED Fixture set | Elect | Supply | SMR11594 | 8200 | EA | 32800
61 | 4 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. | Elect | Labour | SWR10956 | 1268 | EA | 5072
62 | 48 | Labour for Fixing of all types of clamps | Elect | Labour | SWR10917 | 65 | EA | 3120
63 | 60 | Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | Civil | Labour | SWR10860 | 2113 | M3 | 126780
64 | 2 | Room fire extinguisher (2 ltrs capacity) for control room | Elect | Supply | SMR40089 | 4620 | EA | 9240
65 | 12 | Filling with stone dust in basement with 150mm thick layers incldg cost & conveyance all materials watering,consolidation etc complete for finished item of work. | Civil | Labour | SWR33054 | 1062 | M3 | 12744
66 | 10.8 | Earth Work Mass Excavation to a depth as directed, in soils such as Mixture of Gravel and Soft Disintegrated Rock like Shales, Ordinary Gravel, Stoney Earth and Earth Mixed with Fair Sized Boulders and in all conditions such as dry, wet, slurry etc.and in dense or hard soils, disposal and depositing of excavated soil with intial lead of 10 mt and intial lift of 2m or as directed, including cost and conveyance of all materials, ramping and lifting of materials, and labour charges, hire charges of machinery, tools & plants, bailing of water ( either sub soil water, stoMts water, rain water, surface water or of any kind) if any at any stage of work until all works below ground level is finished to the satisfaction ,and from work such as shoring, timbering, strutting with required supports etc. for the work and removal of form work after completion of work etc all complete as directed by the engineer-incharge. | Civil | Labour | SWR33015 | 486 | M3 | 5248.8
67 | 2.7 | Laying Plain C.C (1:4:8) using 40 mm HBG metal including cost & conveyance of all materials labour charges,curing,all leads lifts etc., complete for finished item of work. | Civil | Labour | SWR33028 | 4706 | M3 | 12706.2
68 | 16.2 | C.R.S Masonry in C.M(1:6) using HBG stone including cost & conveyance of all materials labour charges,curing,all leads lifts etc., complete for finished item of work. | Civil | Labour | SWR33041 | 4925 | M3 | 79785
69 | 63 | Plastering of 20mm thick to all uneven faces of walls of superstructure in two coats with base coat in CM 1:5 of 16mm thick and top coat in CM 1:3 4mm thick with dubara sponge finish including cost and conveyance of all materials, water, all labour charges, curing for specified number of days, cutting grooves, all leads, lifts and scaffolding charges,all incidental charges etc. complete for finished item of work and as directed by the Engineer - in - charge. Ground Floor | Civil | Labour | SWR33163 | 520 | M2 | 32760
70 | 6 | S&F of 15 mm brass body CP finish bib tap of not less than 300 grams weight with quarter turn spindle with either internal or external threaded connection conforming to IS 8931 including all operational, incidental and labour charges etc. complete for the finished item of work | Civil | Labour | SWR34330 | 684 | EA | 4104
71 | 40 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007) 22.20mm OD Pipe - SDR 11 including all operational, incidental and labour charges etc. complete for the finished item of work | Civil | Labour | SWR34362 | 313 | M | 12520
72 | 12 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 636
73 | 100 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 11750
74 | 9.8 | Earth Work Mass Excavation to a depth as directed, in soils such as Mixture of Gravel and Soft Disintegrated Rock like Shales, Ordinary Gravel, Stoney Earth and Earth Mixed with Fair Sized Boulders and in all conditions such as dry, wet, slurry etc.and in dense or hard soils, disposal and depositing of excavated soil with intial lead of 10 mt and intial lift of 2m or as directed, including cost and conveyance of all materials, ramping and lifting of materials, and labour charges, hire charges of machinery, tools & plants, bailing of water ( either sub soil water, stoMts water, rain water, surface water or of any kind) if any at any stage of work until all works below ground level is finished to the satisfaction ,and from work such as shoring, timbering, strutting with required supports etc. for the work and removal of form work after completion of work etc all complete as directed by the engineer-incharge. | Civil | Labour | SWR33015 | 486 | M3 | 4762.8
75 | 0.62 | Laying Plain C.C (1:4:8) using 40 mm HBG metal including cost & conveyance of all materials labour charges,curing,all leads lifts etc., complete for finished item of work. | Civil | Labour | SWR33028 | 4706 | M3 | 2917.72
76 | 1.12 | RCC M - 20 Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including all operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work - Footing | Civil | Labour | SWR33098 | 9445 | M3 | 10578.4
77 | 4.06 | RCC M - 20 Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including all operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work - Column Ground floor | Civil | Labour | SWR33100 | 12828 | M3 | 52081.68
78 | 0.2 | Providing High Yield Strength Deformed (HYSD)/ Thermo Mechanically Treated (TMT) / Mild steel (MS) steel bars (Fe 415/ Fe 500 grade as per IS 1786-1979) of different diameters for RCC works , including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying and lap-splicing with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings, including cost and conveyance of steel bars, including all wastages such as overlaps, couplings, chairs, spacer bars including cost and conveyance of binding wire, cover blocks and all incidental, operational, labour charges such as cutting, bending, placing in position, tying excluding taxes on all materials etc., complete for finished item of work in all floors.( APSS No.126) | Civil | Labour | SWR33144 | 84560 | TON | 16912
79 | 100 | S&F of Structural steel of Angles,Channels,Beams etc including fabrication & erection, all incidental, operational, labour charges such as cutting, bending, placing in position, excluding taxes complete for finished item of work. | Civil | Labour | SWR33145 | 119 | KG | 11900
80 | 2.66 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | M3 | 106.4
81 | 5.34 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | M3 | 520.65
Net Total in Rs: | [7 empty] | 2236160.796
GST @ 18 % in Rs. | [7 empty] | 402508.9433
Grand Total in Rs: | [7 empty] | 2638669.7393