## E-Pro Schedule
Name of the work:- Erection of 7.38KM of 33KV Interlinking line on to 33KV Rampally Dayara feeder emanating from 132/33 KV Ghanapur EHT SS with stringing of 6.95KM of SCOH line(100sqmm.AAAC) and laying of 0.43KM of 33KV XLPE 3X400sqmm. UG cable(Double Run) for providing alternate source of supply to 3Nos.33/11KV Substations viz., (i)33/11KV Rampally SS (ii)33/11KV Chakripuram SS (iii)33/11KV Nagaram SS duly tapping at Shivareddygudem and extending up to 33/11 KV Rampally SS along with providing of 33KV bay extension with erection of 33KV VCB at 33/11 KV Rampally SS in Keesara Section in Keesara Sub-Division of Keesara Division in Habsiguda Circle under T&D Improvement to Original Works (under Summer action Plan-2024). (WBS No: T-2331-14-04-01-02-003).
S.No | SAP Code | Estimate Quantity (Only figures) | Item Detailed Specification Description | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item Short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
I. 33KV Bay extension :
1 | SWR10107 | 3 | Excavation of pits in all soils except hard rock requiring blasting for 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | Civil work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 2100
2 | SWR10343 | 3 | Erection of 9.1M long pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Electrical Work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 7200
3 | SWR10356 | 1.62 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 10657.98
4 | SWR10869 | 1.05 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Fabrication Work | Fabrication of struc.with welding. | As per relevent standard specification | 3426 | TO | 3597.3
5 | SWR20769 | 4.8 | Earth work excavation of pits in hard rock requiring blasting.(wherever feasible/ required) | Civil work | Excav. of pit in hard rock req blasting | As per relevent standard specification | 1012.35 | M3 | 4859.28
6 | SWR10460 | 1 | Erection of 33 KV VCB with Control Panel | Electrical Work | Erection of 33kv VCB | As per relevent standard specification | 12500 | EA | 12500
7 | SWR10392 | 2 | Erection of 33 KV AB Switch including alignment and earthing | Electrical Work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 9000
8 | SWR10881 | 2 | Painting ofAB switch OP rods with PO red with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete to Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint | Civil work | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 284
9 | SWR12331 | 2 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Electrical Work | AB Switch Coil Earthing GI No. 8 Wire | As per relevent standard specification | 146.63 | EA | 293.26
10 | SWR11879 | 300 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Electrical Work | Lay-4C/10C 2.5Sqmm Control Cable | As per relevent standard specification | 27 | M | 8100
11 | SWR10942 | 1 | Wiring, commissioning and testing of Outdoor Sub-station switchgear duly conducting the pre commissioning test as per relevent standards & issue of certificate by CEIG authorised testing Engineer | Electrical Work | Testing of Outdoor SS switchgear | As per relevent standard specification | 1825 | EA | 1825
12 | SMR11482 | 4 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Electrical Work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 13944
13 | SWR10357 | 4 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Electrical Work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 4936.8
14 | SWR10359 | 4 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Electrical Work | ERECT. OF LINES-Providing of RCC collar | As per relevent standard specification | 386 | EA | 1544
15 | SWR10920 | 42.55 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication. | Civil work | Laying of earth mat,excavation 75x 8mm | As per relevent standard specification | 65 | RMT | 2765.75
16 | SWR10919 | 83.34 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc with M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Electrical Work | Earthing for raisers of SS Flat 50x6 mm. | As per relevent standard specification | 41 | RMT | 3416.94
17 | SMR11915 | 2 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. | Supply of Material | S-Tension HW 3Bolt 1Zebra/Pnthr 150mm | As per relevent standard specification | 2055 | SET | 4110
18 | SWR10917 | 18 | Labour for Fixing of all types of clamps | Electrical Work | Labour for Fixing of all types of clamps | As per relevent standard specification | 65 | EA | 1170
19 | SWR10198 | 1 | Loading of 33 KV VCBs along with Panel boards | Civil work | LOADING of 33 KV VCBs&Panel boards | As per relevent standard specification | 1024 | EA | 1024
20 | SWR10516 | 1 | Un loading of 33 KV VCBs along with Panel boards | Civil work | UNLOADING of 33 KV VCBs&Panel boards | As per relevent standard specification | 1044.48 | EA | 1044.48
21 | SWR10239 | 2 | Loading of 33KV 800 Amps AB Switch | Civil work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 252
22 | SWR10557 | 2 | Un loading of 33KV 800 Amps AB Switch | Civil work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 158
23 | SWR11220 | 120 | Loading of Unwinding of panther conductor from main drum and recoiling | Civil work | Load-Unwinding Panther conductor | As per relevent standard specification | 3 | M | 360
24 | SWR11221 | 120 | Un loading of Unwinding of panther conductor from main drum and recoiling | Civil work | Unload-Unwinding Panther conductor | As per relevent standard specification | 2 | M | 240
25 | SWR10206 | 1.45 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Civil work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 320.45
26 | SWR10524 | 1.45 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Civil work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 268.25
27 | SWR10133 | 1.45 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) above 20 KM and upto 30 KM | Transportation | TRANSPORT OF STEEL 20 TO 30KM | As per relevent standard specification | 476.34 | TO | 690.693
28 | SWR11862 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) above 20 Km and upto 30 Km with Lorry for each trip | Transportation | Transport of Cond Drum,VCBs >20 & <30Km | As per relevent standard specification | 3691.38 | EA | 3691.38
29 | SMR40009 | 1 | Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. for Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. | Supply of Material | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 2181
30 | SWR10877 | 1 | Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Civil work | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 851
31 | SMR40010 | 1 | Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. for Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. ) | Supply of Material | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 1293
32 | SWR10879 | 1 | Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Civil work | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 482
33 | SWR10963 | 3 | Painting of Name Plates for any equipment | Civil work | Painting of Name Plates for any equipmen | As per relevent standard specification | 122 | EA | 366
34 | SWR10396 | 2 | Erection of 33 KV LAS station/Line type including earthing | Electrical Work | Erect of 33kv LA stn type incl earthing | As per relevent standard specification | 880 | SET | 1760
35 | SMR40013 | 6 | Supply of Spacer T-Clamps with double dropper suitable for Zebra / Panther | Supply of Material | Sup Spacer T-clamps dble dppr zebra/Pant | As per relevent standard specification | 788 | EA | 4728
36 | SMR24942 | 12 | Alluminum alloy Pad clamps minimum 15 mm Thickness, 75 mm Width 150 Mm Length conforming to IS:5561-1970, IS 617, IS 2633-1964, IS 1363-1967, IS1367-1961), Six bolted with hot dip galvanized bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 ") minimum weight of 900 gms to suit for Panther ACSR Conductor of pad size 75 X 75 X 15mm for carrying 600 A current. | Supply of Material | S-Al PadClamp 6Bolt15mm thck for Panther | As per relevent standard specification | 360 | EA | 4320 | 149244.56
37 | SWR11701 | 300 | Loading of PVC Control Cable 10 Core | Civil work | Load-PVC Control Cable 10C | As per relevent standard specification | 1 | M | 300 | 1375361.71
38 | SWR11712 | 300 | Un loading of PVC Control Cable 10 Core | Civil work | UnLoad-PVC Control Cable 10C | As per relevent standard specification | 1.02 | M | 306 | 1121347.45
39 | SWR20685 | 6 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | Civil work | Cement concrete with 40MM metal VCB plin | As per relevent standard specification | 5160 | M3 | 30960 | 2548921.62
40 | SWR10884 | 6 | Bus Stringing: Connection of equipment to bus and or another equipment with single zebra/Panther conductor including easuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Electrical Work | Conn. of equip/bus single zebra/panther | As per relevent standard specification | 224 | EA | 1344 | 391513.16
II. 33KV Line:
41 | SWR22092 | 6.95 | survey line&cable including, peg marking &tree clearence | Civil work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 5316.75
42 | SWR10108 | 76 | Excavation of pits in all soils except hard rock requiring blasting for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M (1.31 cum) | Civil work | EXCAV. OF PIT 0.75 M x 0.9 M x 1.95 M | As per relevent standard specification | 629.85 | EA | 47868.6
43 | SWR11040 | 40 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Civil work | Ex of Hard pit w/o blast 0.75X0.9X1.95M | As per relevent standard specification | 990.68 | EA | 39627.2
44 | SWR10113 | 6 | Excavation of pits in hard rock requiring blasting. (other than SS) for 11Mtrs PSCC Pole/ Box poles 0.75 M x 0.9 M x 1.95 M | Civil work | EXCAV OF PIT HARD 0.75 Mx0.9 Mx1.95 M | As per relevent standard specification | 1326 | EA | 7956
45 | SWR10107 | 9 | Excavation of pits in all soils except hard rock requiring blasting for 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | Civil work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 6300
46 | SWR11039 | 1 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Civil work | Exca Hard pit w/o blast 0.76X0.76X1.83M | As per relevent standard specification | 928 | EA | 928
47 | SWR11267 | 8 | Erection of 12Meter Box pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Electrical Work | Erect-12Meter Box pole | As per relevent standard specification | 3901.37 | EA | 31210.96
48 | SWR10642 | 8 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Fabrication Work | Fabrication of 175x85/150x75mm RS joist | As per relevent standard specification | 512.55 | EA | 4100.4
49 | SWR10640 | 8 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Civil work | Painting of RS Joist(1C RO, 2C Al.Paint) | As per relevent standard specification | 1132 | EA | 9056
50 | SWR10978 | 114 | Erection of 11M pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Electrical Work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4336.85 | EA | 494400.9
51 | SWR11083 | 6 | Erection of 9.1M pole for stuts in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Electrical Work | Erec of 9.1 Mts PSCC poles for stuts | As per relevent standard specification | 2400 | EA | 14400
52 | SWR10366 | 6.95 | Paving out and stringing of 33KV 100sqmm 3 condutor conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location. | Electrical Work | Stringing 100sqmm 33/11kv Line 3 Cond SC | As per relevent standard specification | 13856.7 | KM | 96304.065
53 | SWR10653 | 18 | Formation of horizontal Cut point for 11 KV Single Circuit line excluding pole erection and stays | Electrical Work | Formatn of Horiz Cut point for 11KV line | As per relevent standard specification | 1435.81 | EA | 25844.58
54 | SWR10319 | 132 | Fabrication of Back clamps with 75 x 8 mm MS Flat including 2 coats of Red oxide painting | Fabrication Work | Fab Back clamps with 75 x 8 mm MS Flat | As per relevent standard specification | 31 | EA | 4092
55 | SWR10320 | 63 | Fabrication of Back clamps with 50 x 6 mm MS Flat including 2 coats of Red oxide painting | Fabrication Work | Fab Back clamps with 50 x 6 mm MS Flat | As per relevent standard specification | 15 | EA | 945
56 | SWR10312 | 60 | Fabrication of 1.53 mt. V.Cross arms with 100x50 mm MS Channel materials including 2 coats of Red oxide painting | Fabrication Work | Fab V.Cross arms with 100x50 mm MS Chan | As per relevent standard specification | 158 | EA | 9480
57 | SWR11269 | 60 | Fixing of 11KV Side Arm along with Cross Arm including angle strut up to 5 feet | Electrical Work | Fix-Side/Cross Arm incl strut fr 11KV | As per relevent standard specification | 455 | EA | 27300
58 | SWR11180 | 114 | Sub-transport of 11M poles upto Workspot upto 10KM (Including loading and unloading) | Transportation | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 49244.58
59 | SWR20308 | 10 | Sub-transport of 9.1M poles upto Workspot upto 10KM (Including loading and unloading) | Transportation | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 4072.9
60 | SWR10356 | 44.795 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 294706.305
61 | SWR11890 | 0.248 | Mass Concreting for pole for Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt. | Civil work | Coping & Muffing-Iron Pole | As per relevent standard specification | 3892.98 | M3 | 965.459
62 | SWR10378 | 136 | Painting of poles for Numbering of poles incl. cost of paint | Civil work | Numbering of poles incl. cost of paint | As per relevent standard specification | 32 | EA | 4352
63 | SWR10134 | 7.105 | Transport of iron materials Above 30 KM and upto 50 KM such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) | Transportation | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 4174.3296
64 | SWR11862 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Above 20 Km and upto 30 Km with Lorry for each trip | Transportation | Transport of Cond Drum,VCBs >20 & <30Km | As per relevent standard specification | 3691.38 | EA | 14765.52
65 | SWR10206 | 7.105 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Civil work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 1570.205
66 | SWR10191 | 7 | Loading of Conductor drums | Civil work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 1414
67 | SWR10509 | 7 | Un loading of Conductor drums | Civil work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 700
68 | SWR10204 | 4 | LOADING of R.S. Joists 175 x 85 mm | Civil work | LOADING of R.S. Joists 175 x 85 mm | As per relevent standard specification | 76 | EA | 304
69 | SWR10522 | 4 | UNLOADING of R.S. Joists 175 x 85 mm | Civil work | UNLOADING of R.S. Joists 175 x 85 mm | As per relevent standard specification | 50 | EA | 200
70 | SWR10211 | 49 | LOADING of 33 KV Pin insulators | Civil work | LOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | KI | 147
71 | SWR10529 | 49 | UNLOADING of 33 KV Pin insulators | Civil work | UNLOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | KI | 147
72 | SWR12416 | 11 | LOADING of 33 & 11 KV Disc insulators | Civil work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | KI | 22
73 | SWR10392 | 2 | Erection of 33 KV AB Switch including alignment and earthing | Electrical Work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 9000
74 | SWR10881 | 2 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete to Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Civil work | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 284
75 | SWR12331 | 2 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Electrical Work | AB Switch Coil Earthing GI No. 8 Wire | As per relevent standard specification | 146.63 | EA | 293.26
76 | SWR10239 | 2 | LOADING of 33 KV AB SWCH Con 400/800 A | Civil work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 252
77 | SWR10557 | 2 | UNLOADING of 33 KV AB SWCH Con 400/800 A | Civil work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 158
78 | SMR11483 | 2 | Supply of CI eath pipe with 80mm dia,2.75 M Length | Supply of Material | S-CI Pipe earthing 80mm dia 2.75m long | As per relevent standard specification | 2789 | EA | 5578
79 | SWR10357 | 2 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Electrical Work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 2468.4
80 | SWR10359 | 2 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Electrical Work | ERECT. OF LINES-Providing of RCC collar | As per relevent standard specification | 386 | EA | 772
81 | SWR10920 | 40 | Laying of earth mat with 75x 8mm MS Flat / GI Flat.including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication. | Electrical Work | Laying of earth mat,excavation 75x 8mm | As per relevent standard specification | 65 | RMT | 2600
82 | SWR12125 | 66.67 | Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete | Electrical Work | Run-GI Earth Flat 25x3mm from metallic p | As per relevent standard specification | 14.03 | M | 935.3801
83 | SWR23200 | 10000 | Cut-Tree Branch(LT/11/33)&Trnsprt Debris | Civil work | Cut-Tree Branch(LT/11/33)&Trnsprt Debris | As per relevent standard specification | 4 | EA | 40000
84 | SWR11308 | 2 | Restringing of existing 55 Sqmm single ckt 3 cond loose Lines by removing the pin-binding and jumpers, Providing of temporary stays, providing stiffners pieces, replacement of damaged insulators, alignment of cross arms, pin binding and jumpering after tensioning and removing of the temporary stays complete . | Electrical Work | Restring-55 Sqmm SC-3 Conductors | As per relevent standard specification | 6616 | KM | 13232
85 | SWR20190 | 400 | Removing and Reconnection of LT Services | Electrical Work | Removing and Reconnection of LT Services | As per relevent standard specification | 44 | EA | 17600
86 | SWR11720 | 38 | Fabrication of 11KV side arm 75x40mm Channel 65x65x6mm Angle | Fabrication Work | Fabricate-11KV Side Arm | As per relevent standard specification | 100 | EA | 3800
87 | SWR10319 | 126 | Fabrication of Back clamps with 75 x 8 mm MS Flat materials including 2 coats of Red oxide painting | Fabrication Work | Fab Back clamps with 75 x 8 mm MS Flat | As per relevent standard specification | 31 | EA | 3906
88 | SWR11320 | 20 | Dismantling of 9.1M PSCC Pole Damaged Poles, not required and available in the middle of roads, transporting to stock point etc. | Electrical Work | Dismantle-9.1 M long PSCC pole | As per relevent standard specification | 948.09 | EA | 18961.8
89 | SWR21190 | 20 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits any and leveling the site with out any lead.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Civil work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 10400
90 | SWR10354 | 20 | Assembly and erection of 33KV stay set including fixing of guy insulators, clamps etc., on the pole and fixing stay wire and binding securely on either side as per standards, transport of material from road side to location and back filling with earth ramming | Electrical Work | Assembly and erection of Stay set 33kv | As per relevent standard specification | 684.53 | SET | 13690.6
91 | SWR11312 | 1.5 | Restringing of existing LT 3-Ph 34Sqmm 5 Conductor loose Lines by removing the pin-binding and jumpers, Providing of temporary stays, providing stiffners pieces, replacement of damaged insulators, alignment of cross arms, pin binding and jumpering after tensioning and removing of the temporary stays complete . | Electrical Work | Restring-LT 3-Ph 34Sqmm 5 Conducto | As per relevent standard specification | 7795 | KM | 11692.5
92 | SMR11485 | 40 | Supply of GI Flat 25X3 mm | Supply of Material | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 4200
93 | SWR10343 | 4 | Erection of 9.1M PSCC pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation for 9.1 M long PSCC pole | Electrical Work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 9600
94 | SWR10307 | 1000 | Drilling of holes upto 20 mm dia using power drills on MS Channel, Angles and flat | Fabrication Work | FABR-Drilling of holes upto 20 mm dia 4 | As per relevent standard specification | 4 | EA | 4000
95 | SWR10631 | 11 | Un loading of 33 & 11 KV Disc insulators | Civil work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | KI | 22
III. 33KV Railway Crossing:
96 | SWR11972 | 10 | Laying of DR 33KV 3x400sqmm XLPE UG cable Double Run In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Video shoot of cable &GIS coordinates and tagging of starting of cable, joints of cable and ending of cable. Auto CAD drawings of cable path is to be maintained. | Electrical Work | Lay-DR 33KV 3x400sqmm UG Cb HG/BC/CC/BT | As per relevent standard specification | 749 | M | 7490
97 | SMR11485 | 25 | Supply of GI Flat 25X3 mm | Supply of Material | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 2625
98 | SMR40082 | 30 | Supply of 9" B Class GI pipe 7.3mm thck 28.8Kg/M | Supply of Material | S-9" B Class GI pipe 7.3mm thck 28.8Kg/M | As per relevent standard specification | 1113 | M | 33390
99 | SMR12227 | 8 | Supply of 33kV cable support cable clamps& nuts | Supply of Material | S-33KV Cb Support Cb Clamps & Nuts | As per relevent standard specification | 500 | EA | 4000
100 | SWR10387 | 4 | Making of 33 KV 3x400 Sqmm Cable Outdoor/Indoor End Termination | Electrical Work | OD/Idoor end termination 33kv 3x400 xlpe | As per relevent standard specification | 2764.76 | EA | 11059.04
101 | SMR11483 | 2 | Supply of CI eath pipe with 80mm dia,2.75 M Length | Supply of Material | S-CI Pipe earthing 80mm dia 2.75m long | As per relevent standard specification | 2789 | EA | 5578
102 | SWR10357 | 2 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Electrical Work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 2468.4
103 | SWR10307 | 20 | Drilling of holes upto 20 mm dia using power drills on MS Channel, Angles and flat | Fabrication Work | FABR-Drilling of holes upto 20 mm dia 4 | As per relevent standard specification | 4 | EA | 80
104 | SWR10294 | 40 | Cutting charges for MS Channel 100 x 50 mm | Civil work | Cutting Charges for MS chanl 100x50mm | As per relevent standard specification | 10 | EA | 400
105 | SWR11230 | 1 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Civil work | Load-11/33KV XLPE UG Cable for all sizes | As per relevent standard specification | 1024 | DR | 1024
106 | SWR11231 | 1 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Civil work | Unload-11/33KV XLPE UG Cable all sizes | As per relevent standard specification | 1024 | DR | 1024
107 | SWR11862 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Above 20 Km and upto 30 Km with Lorry for each trip | Transportation | Transport of Cond Drum,VCBs >20 & <30Km | As per relevent standard specification | 3691.38 | EA | 3691.38
108 | SWR11171 | 4 | Loading of 33/11KV XLPE UG Cable End Termination Kits for all sizes | Civil work | Loading of 11/33 KV IN/OUT door kits | As per relevent standard specification | 6 | EA | 24
109 | SWR11152 | 4 | Un-loading of 11/33 KV IN/OUT door kits | Civil work | Un-loading of 11/33 KV IN/OUT door kits | As per relevent standard specification | 4 | EA | 16
110 | SWR11001 | 100 | Laying of double run 33KV UG cable by HDD method with casing HDPE pipe of 160mm PN4 PE 80 as per IS4984. Video shoot of cable &GIS coordinates and tagging of starting of cable, joints of cable and ending of cable. Auto CAD drawings of cable path is to be maintained. | Civil work | HDD cable with HDPE pipe in Hard rock | As per relevent standard specification | 6993 | M | 699300
111 | SWR24771 | 320000 | * Railway Crossing Permission Charges Important Note: Railway crossing permission charges provided in sl.no. 111 of the above schedule, subject to condition that producing of the actual payment to the railway department. | Civil work | Railway Crossing Permission Charges | As per relevent standard specification | 1 | LS | 320000
112 | SWR12004 | 40 | Raising of double run to 33 KV 3x400 Sqmm Cable cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Electrical Work | Raise-DR 33KV 3x400sqmm UG Cb on support | As per relevent standard specification | 323.85 | M | 12954
113 | SMR40077 | 30 | Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | Supply of Material | Supply of 250 mm Hume pipe of class NP3 | As per relevent standard specification | 363 | M | 10890
114 | SWR12125 | 41.67 | Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete | Electrical Work | Run-GI Earth Flat 25x3mm from metallic p | As per relevent standard specification | 14.03 | M | 584.6301
115 | SMR40085 | 4 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Supply of Material | Supply of Pre-cast cable Joint markers | As per relevent standard specification | 484 | EA | 1936
116 | SWR10359 | 2 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Electrical Work | ERECT. OF LINES-Providing of RCC collar | As per relevent standard specification | 386 | EA | 772
117 | SWR10988 | 10 | Laying of 2nd cable in excavated trench. | Electrical Work | Lay-2nd Cable in Excavated Trench | As per relevent standard specification | 204.1 | M | 2041
IV. Towers:
118 | SMR11683 | 10 | Supply of M+3 Tower (Galvanized) as per DATA-VII SSR 2020-21 | Supply of Material | S-M+3 Tower GALV | As per relevent standard specification | 140674.3 | EA | 1406743
119 | SWR11850 | 10 | Erection of M+3 Tower (Galvanized) as per DATA-VII SSR 2020-21 | Electrical Work | Erect- M+3 Tower GALV | As per relevent standard specification | 64576 | EA | 645760
120 | SMR11684 | 10 | Supply of material for Extension of 3Mtrs for M+3 (Galvanized) as per DATA-VII SSR 2020-21 | Supply of Material | S-Mat. for Extn of M+3 Tower by 3M GALV | As per relevent standard specification | 28520.64 | EA | 285206.4
121 | SWR11851 | 10 | Erection of Extension of 3Mtrs for M+3 (Galvanized) as per DATA-VII SSR 2020-21 | Electrical Work | Erect-Extn of 3M for M+3 Tower GALV | As per relevent standard specification | 5168.95 | EA | 51689.5
122 | SMR11684 | 4 | Supply of material for Extension of 3Mtrs for M+3 (Galvanized) as per DATA-VII SSR 2020-21 | Supply of Material | S-Mat. for Extn of M+3 Tower by 3M GALV | As per relevent standard specification | 28520.64 | EA | 114082.56
123 | SWR11851 | 4 | Erection of Extension of 3Mtrs for M+3 (Galvanized) as per DATA-VII SSR 2020-21 | Electrical Work | Erect-Extn of 3M for M+3 Tower GALV | As per relevent standard specification | 5168.95 | EA | 20675.8
124 | SWR12085 | 7 | Excavation of pits in all soils except hard rock requiring blasting for M-Type Tower (1.2M x 1.2M x 3.3M ) 4.752cum | Civil work | Excvt Pit ext HardBlst 1.2Mx1.2Mx3.3M | As per relevent standard specification | 1997.93 | EA | 13985.51
125 | SWR12090 | 3 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) for M-Type Tower (1.2M x 1.2M x 3.3M ) 4.752cum | Civil work | Excvt Pit Hard w/o Blst 1.2Mx1.2Mx3.3M | As per relevent standard specification | 3592.95 | EA | 10778.85
V. 33KV ORR Crossing:
126 | SWR11972 | 190 | Laying of XLPE UG cable Double Run In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC including excavation of trench of size 1200mm for 33 KV 3x400 sqmm cable from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.in In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC. Video shoot of cable &GIS coordinates and tagging of starting of cable, joints of cable and ending of cable. Auto CAD drawings of cable path is to be maintained. | Electrical Work | Lay-DR 33KV 3x400sqmm UG Cb HG/BC/CC/BT | As per relevent standard specification | 749 | M | 142310
127 | SWR11988 | 20 | Laying of XLPE UG cable Double Run Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) including excavation of trench of size 1200mm for 33 KV 3x400 sqmm cable from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc. .(Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe). Video shoot of cable &GIS coordinates and tagging of starting of cable, joints of cable and ending of cable. Auto CAD drawings of cable path is to be maintained. | Electrical Work | Lay-DR 33KV 3x400sqmm UG Cb CC/BT RdCrsg | As per relevent standard specification | 1587.07 | M | 31741.4
128 | SWR12004 | 40 | Raising of double run 33KV 3x400sqmm cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Electrical Work | Raise-DR 33KV 3x400sqmm UG Cb on support | As per relevent standard specification | 323.85 | M | 12954
129 | SWR10387 | 4 | Making of Outdoor/Indoor End Termination of 33KV 3x400 Sqmm Cable | Electrical Work | OD/Idoor end termination 33kv 3x400 xlpe | As per relevent standard specification | 2764.76 | EA | 11059.04
130 | SMR40077 | 210 | Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | Supply of Material | Supply of 250 mm Hume pipe of class NP3 | As per relevent standard specification | 363 | M | 76230
131 | SMR40085 | 4 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Supply of Material | Supply of Pre-cast cable Joint markers | As per relevent standard specification | 484 | EA | 1936
132 | SMR11483 | 2 | Supply of CI eath pipe with 80mm dia,2.75 M Length | Supply of Material | S-CI Pipe earthing 80mm dia 2.75m long | As per relevent standard specification | 2789 | EA | 5578
133 | SWR10357 | 2 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Electrical Work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 2468.4
134 | SMR11485 | 40 | Supply of GI Flat 25X3 mm | Supply of Material | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 4200
135 | SWR12125 | 66.67 | Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete | Electrical Work | Run-GI Earth Flat 25x3mm from metallic p | As per relevent standard specification | 14.03 | M | 935.3801
136 | SWR11230 | 2 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Civil work | Load-11/33KV XLPE UG Cable for all sizes | As per relevent standard specification | 1024 | DR | 2048
137 | SWR11231 | 2 | Unload-11/33KV XLPE UG Cable all sizes | Civil work | Unload-11/33KV XLPE UG Cable all sizes | As per relevent standard specification | 1024 | DR | 2048
138 | SWR11862 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) above 20 Km and upto 30 Km with Lorry for each trip | Transportation | Transport of Cond Drum,VCBs >20 & <30Km | As per relevent standard specification | 3691.38 | EA | 3691.38
139 | SMR11487 | 20 | Supply of MS bolts & nuts and washers etc of all sizes | Supply of Material | S-MS Bolts & Nuts,Washers etc., | As per relevent standard specification | 91.25 | KG | 1825
140 | SMR40082 | 30 | Supply of 9" B Class GI pipe 7.3mm thck 28.8Kg/M | Supply of Material | S-9" B Class GI pipe 7.3mm thck 28.8Kg/M | As per relevent standard specification | 1113 | M | 33390
141 | SWR10988 | 210 | Laying of 2nd cable in excavated trench | Electrical Work | Lay-2nd Cable in Excavated Trench | As per relevent standard specification | 204.1 | M | 42861
142 | SWR10359 | 2 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Electrical Work | ERECT. OF LINES-Providing of RCC collar | As per relevent standard specification | 386 | EA | 772
143 | SMR12227 | 8 | Supply of 33kV cable support cable clamps& nuts | Supply of Material | S-33KV Cb Support Cb Clamps & Nuts | As per relevent standard specification | 500 | EA | 4000
144 | SWR11171 | 4 | Loading of 33/11KV XLPE UG Cable End Termination Kits for all sizes | Civil work | Loading of 11/33 KV IN/OUT door kits | As per relevent standard specification | 6 | EA | 24
145 | SWR11152 | 4 | Un loading of 33/11KV XLPE UG Cable End Termination Kits for all sizes | Civil work | Un-loading of 11/33 KV IN/OUT door kits | As per relevent standard specification | 4 | EA | 16
146 | SWR11172 | 2 | Loading of 33/KV XLPE UG CableStraight Through Joint Kits for all sizes | Civil work | Loading 11/33KV Straight thr jointkit | As per relevent standard specification | 8 | EA | 16
147 | SWR11153 | 2 | Un loading of 33/KV XLPE UG CableStraight Through Joint Kits for all sizes | Civil work | Un-loading 11/33KV Straight thr jointkit | As per relevent standard specification | 4 | EA | 8
148 | SWR10382 | 2 | Making of Straight through joints to 33 KV 3x400 Sqmm Cable | Electrical Work | Straight through joint 33kv 3x400 xlpe | As per relevent standard specification | 5700.78 | EA | 11401.56
Service Cost: | [8 empty] | 5586388.4869
[7 empty] | GST @18% |  | 1005549.9276
TOTAL | [8 empty] | 6591938.4146
*