## Manikonda golconda
Name of the Work : providing of 3rd alternate source to 33/11KV Golconda SS by laying of 5.25KM of 3X400Sqmm. XLPE UG Cable (Triple Run) from 132/33KV Manikonda EHT SS to the 33/11KV Golconda SS viz., 2run for providing of 3rd alternate source to 33/11kV Golconda SS and 1 run for extending regular source of supply to the upcoming 33/11KV Pride India SS of Golconda operation Section in Golconda Subdivision in Mehdipatnam Division in Hyderabad Central Circle and work executed by the Master plan SD-VI Sub-Division of MP-1 Division of Hyderabad Master plan Circle under T& D Improvement Works(Summer Action Plan 2025).
WBS Element : T-2427-12-01-03-01-001
8 Column Schedule
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | Service Codes | Rate (INR) | UOM | AMOUNT
1 | 5.25 | survey line&cable including peg mark & tree clear | Elect | Labour | SWR22092 | 765 | KM | 4016.25
2 | 49 | Loading of 11KV/33KV XLPE UG Cable Drum for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 50176
3 | 38 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Upto 10 Km with Lorry for each trip | Elect | Labour | SWR11860 | 2720.34 | EA | 103372.92
4 | 49 | Un loading of 11KV/33KV XLPE UG Cable Drum for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 50176
5 | 4300 | Laying of XLPE UG cable Triple or more Run including excavation of trench of size 1000mm wide to 750mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Along the CC / BT multi layer road requiring compressor-33 KV 3x400 Sqmm Cable | Elect | Labour | SWR12019 | 1731.45 | M | 7445235
6 | 650 | Laying of XLPE UG cable Triple or more Run including excavation of trench of size 1000mm wide to 750mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe)-33 KV 3x400 Sqmm Cable | Elect | Labour | SWR12024 | 1978.8 | M | 1286220
7 | 300 | Laying of 33kV XLPE UG Cable Triple run and above in Hard rock ( 1.2x0.75x1 = 0.9 cum) | Elect | Labour | SWR11800 | 2733.6 | M | 820080
8 | 9900 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 204.1 | M | 2020590
9 | 150 | Raising of Single Run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11954 | 135.66 | M | 20349
10 | 70 | Supply & Erection of Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 192150
11 | 59 | Making of 33KV 3X400Sq.mm XLPE UG Cable Straight through joints | Elect | Labour | SWR10382 | 5700.78 | EA | 336346.02
12 | 1200 | Supply of 6" B class GI pipe Cost of Pipes and slabs | Elect | Supply | SMR40081 | 1044 | M | 1252800
13 | 350 | supply of 6" DWC pipe | Elect | Supply | SMR11610 | 1012 | M | 354200
14 | 1900 | Supply of Hume Pipe Size 9" size | Elect | Supply | SMR40001 | 125 | M | 237500
15 | 18 | Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination | Elect | Labour | SWR10387 | 2764.76 | EA | 49765.68
16 | 4850 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 145500
17 | 1.28 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 282.88
18 | 1.28 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 236.8
19 | 16 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 1216
20 | 5.28 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel,iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading )-Above 10 KM and upto 20 KM | Elect | Labour | SWR10132 | 412.08 | TO | 2175.7824
21 | 16 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 800
22 | 8 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 4100.4
23 | 16 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxide and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 18112
24 | 8 | Excavation of pits in hard rock not requiring blasting for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 7925.44
25 | 8 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | Elect | Labour | SWR11267 | 3901.37 | EA | 31210.96
26 | 80.85 | Laying of MS Flats /GI Flats 75x 8mm earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment andconnecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes including fabrication | Elect | Labour | SWR10920 | 65 | RMT | 5255.25
27 | 8.4 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 55263.6
28 | 0.248 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3892.98 | M3 | 965.459
29 | 2 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | SET | 1760
30 | 4 | LOADING of 33 KV AB SWCH Con 400/800 A | Elect | Labour | SWR10239 | 126 | EA | 504
31 | 4 | UNLOADING of 33 KV AB SWCH Con 400/800 A | Elect | Labour | SWR10557 | 79 | EA | 316
32 | 4 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 4500 | EA | 18000
33 | 8 | Supply of CI eath pipe with 80mm dia,2.75 M Length | Elect | Supply | SMR11483 | 2789 | EA | 22312
34 | 8 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 9873.6
35 | 8 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 3088
36 | 49 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters, CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 23716
37 | 16 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 848
38 | 100 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 11750
39 | 1 | Submission of auto CAD Drawing as per pole schedule (Detailed survey and sketch)-Up to 10 km | Elect | Labour | SWR12104 | 6000 | LS | 6000
40 | 4 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 568
41 | 4 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 586.52
42 | 0.9 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 3083.4 | 14598426.9614 | -14598426.9614
43 | 8 | Supplying of 33KV 1Cx400Sqmm PlugTerminationKit | Elect | Supply | SMR24773 | 90915 | EA | 727320
44 | 8 | Making of Outdoor/Indoor End Termination Inst-33KV 1Cx400Sqmm PlugTerminationKit | Elect | Labour | SWR24773 | 15675 | EA | 125400
45 | 8 | Supply of 33KV 1Cx400Sqmm O/d Cb End Kit | Elect | Supply | SMR24774 | 6792.5 | EA | 54340
46 | 8 | Making of Outdoor/Indoor End Termination Inst-33KV 1Cx400Sqmm O/d Cb End Kit | Elect | Labour | SWR24774 | 3030.5 | EA | 24244
47 | 40 | Supply of Earth Mat 100x16mm GI Flat from Earth | Elect | Supply | SMR23228 | 975 | M | 39000
48 | 40 | Laying of MS/GI 100x16mm earth flat | Elect | Labour | SWR22054 | 65 | RMT | 2600
49 | 2 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | SET | 1760
50 | 2 | Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10239 | 126 | EA | 252
51 | 2 | Un loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10557 | 79 | EA | 158
52 | 2 | Erection of AB Switch and aligment complete including alignment and earthing | Elect | Labour | SWR10392 | 4500 | EA | 9000
53 | 2 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting 33 KV DP Structure with 175x85/150x75mm RS joist | Elect | Labour | SWR11276 | 5670 | SET | 11340
54 | 1.39 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 307.19
55 | 1.39 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 257.15
56 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-RS Joists 150x75/175 x 85 mm | Elect | Labour | SWR10346 | 1934 | EA | 7736
57 | 12 | LOADING of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 912
58 | 12 | UNLOADING of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 600 |  | 15603053.3014
59 | 12 | Fabrication of Poles , 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 6150.6
60 | 4.39 | Painting of sub-station structures with two coats ofaluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of substation structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.Supply of material cost for First coat of 1st Grade AluminiumPaint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 9574.59
61 | 4.39 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of substation structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 3735.89
62 | 4.39 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of substationstructures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete.Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elect | Supply | SMR40010 | 1293 | TO | 5676.27
63 | 4.39 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of substation structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium | Elect | Labour | SWR10879 | 482 | TO | 2115.98
64 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 3962.72
65 | 7.72 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 50789.88
66 | 0.124 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3892.98 | M3 | 482.7295
67 | 2 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 284
68 | 2 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 293.26
69 | 4 | Supply of CI eath pipe with 80mm dia,2.75 M Length | Elect | Supply | SMR11483 | 2789 | EA | 11156
70 | 4 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 4936.8
71 | 4 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elect | Labour | SWR10359 | 386 | EA | 1544
72 | 3 | Loading of 11/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 3072
73 | 3 | Unloading of 11/33KV XLPE UG Cable all sizes | Elect | Labour | SWR11231 | 1024 | DR | 3072
74 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 6599.4
75 | 1.62 | Earth work excavation for foundations and depositing on bank for all lifts and with an iniutial lead of 10m including all operational, incidental, labour charges such as shoring, sheeting, planking, strutting, etc. complete for finished item of work including seigniorage excluding dewatering charges etc as per SS - 20 B (APSS 308).Hard rock ( blasting prohibited ) | Civil | Labour | SWR33018 | 1440 | M3 | 2332.8
76 | 1.08 | Laying Plain C.C (1:4:8) using 40 mm HBG metal including cost & conveyance of all materials labour charges,curing,all leads lifts etc., complete for finished item of work. | Civil | Labour | SWR33028 | 4706 | M3 | 5082.48
77 | 2.48 | Brick masonry in cement mortar (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts etc., complete for finished item of work - Ground Floor | Civil | Labour | SWR33068 | 7209 | M3 | 17878.32
78 | 36 | Plastering of 20mm thick to all uneven faces of walls of superstructure in two coats with base coat in CM 1:5 of 16mm thick and top coat in CM 1:3 4mm thick with dubara sponge finish including cost and conveyance of all materials, water, all labour charges, curing for specified number of days, cutting grooves, all leads, lifts and scaffolding charges,all incidental charges etc. complete for finished item of work and as directed by the Engineer - in - charge. Ground Floor | Civil | Labour | SWR33163 | 520 | M2 | 18720
79 | 12.15 | Filling with gravel in basement with 150mm thick layers incldg cost & conveyance all materials watering,consolidation etc complete for finished item of work. | Civil | Labour | SWR33052 | 480 | M3 | 5832
80 | 12.15 | Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | Elect | Labour | SWR10860 | 2113 | M3 | 25672.95
81 | 8 | Core Cutting of Reinforcement Wall | Elect | Labour | SWR12328 | 3150 | M3 | 25200
82 | 36 | Providing and applying Surya Cem of three coats of approved brand and shade to give an even shade after thoroughly brushing the surface to remove all dirt and remains of loose powdered materials, including cost and conveyance of all materials to work site and all operational, incidental, labour charges etc. complete for finished item of work | Civil | Labour | SWR33329 | 85 | M2 | 3060
83 | 110 | Laying of Single Run XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.Along the CC / BT multi layer road requiring compressor-33kV 1x400 Sqmm Cu cable | Elect | Labour | SWR11935 | 887.4 | M | 97614
84 | 770 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 204.1 | M | 157157
85 | 200 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 204.1 | M | 40820
86 | 120 | Raising of Single Run cable on already erected support with wooden / MS clamps andconnecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-33kV 1x400 Sqmm Cu cable | Elect | Labour | SWR11962 | 121.13 | M | 14535.6
87 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elect | Labour | SWR11039 | 928 | EA | 3712 | 1536289.6095
| Sub Total: | [6 empty] | 16134716.571 | 16134716.571
| 18% Service tax on labour | [6 empty] | 2904248.9828
| Total Rs. | [6 empty] | 19038965.5537 | 19038965.5537
380779.3111
17226143.8128
1812821.7398
19038965.5526

## Jonnabanda (hidden)
Name of the Work : Erection of new 33/11kV Outdoor SS with 2X8 MVA PTRs and 8 Nos. 11kV Feeders at JonnaBanda SS
WBS Element : S-1660-12-01-02-01-001
8 Column Schedule
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | Service Codes | Rate (INR) | UOM | AMOUNT
1 | 8 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elect | Supply | SMR11482 | 3486 | EA | 27888
2 | 8 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 9873.6
3 | 1 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 1024
4 | 1 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 1024
5 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 3299.7
6 | 115 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts,-Along the CC / BT multi layer road requiring compressor-11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11981 | 1264.64 | M | 145433.6
7 | 20 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts,-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders /Normal soil/CC-11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11973 | 631.06 | M | 12621.2
8 | 135 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 204.1 | M | 27553.5
9 | 5 | Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | Elect | Labour | SWR10391 | 2370.63 | EA | 11853.15
10 | 0.25 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel,iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading )-Above 10 KM and upto 20 KM | Elect | Labour | SWR10132 | 412.08 | TO | 103.02
11 | 2 | Supply of Danger boards with clamps | Elect | Supply | SMR40070 | 116 | EA | 232
12 | 1 | Geophysical Investgation Charges | Elect | Labour | SWR33608 | 5000 | EA | 5000
13 | 300 | Drill-165mm Bore Well 270M and above | Elect | Labour | SWR34836 | 1082 | M | 324600
14 | 35 | S&F 160mm dia PVC Casing | Elect | Labour | SWR33611 | 883 | M | 30905
15 | 1.5 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel,iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading )-Above 10 KM and upto 20 KM | Elect | Labour | SWR10132 | 412.08 | TO | 618.12
16 | 8 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elect | Labour | SWR10359 | 386 | EA | 3088
17 | 270 | Supply of 4" B class GI pipe | Elect | Supply | SMR40080 | 740 | M | 199800
18 | 372.34 | Laying of earth mat including excavation of trenches of depth 600mm, welding,connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication.-75x 8mm MS Flat / GI Flat. | Elect | Labour | SWR10920 | 65 | RMT | 24202.1
19 | 1.75 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Elect | Labour | SWR10206 | 221 | TO | 386.75
20 | 1.75 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Elect | Labour | SWR10524 | 185 | TO | 323.75
21 | 1 | Supply & Erection of SP SubMrsbl Pumpset | Elect | Supply | SWR33640 | 48007 | EA | 48007 | 877836.49
22 | 16 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 | Elect | Supply | SMR40051 | 13913 | EA | 222608 | 222608 | 0
23 | 16 | Erection of tubular poles | Elect | Labour | SWR10955 | 1379 | EA | 22064 | 22064 | 0
24 | 16 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE /CROMPTON/ BAJAJ/VIN/ WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE /NICHIA/OSRAM/ SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing,toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty-90W LED Fixture set | Elect | Supply | SMR11594 | 8200 | EA | 131200 | 131200 | 0
25 | 16 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. | Elect | Labour | SWR10956 | 1268 | EA | 20288 | 20288 | 0
26 | 52 | Excavation of pits in hard rock requiring blasting. (other than SS)-9.1Mtrs PSCC Pole 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elect | Labour | SWR10112 | 1770 | EA | 92040 | 92040 | 0
27 | 52 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-R.S. Joists 150 x 150 mm | Elect | Labour | SWR10348 | 1952.61 | EA | 101535.72 | 101535.72 | 0
28 | 52 | Loading of R.S. Joists 150 x 150mm / Rail poles | Elect | Labour | SWR10205 | 176 | EA | 9152 | 9152 | 0
29 | 52 | Un-Loading of R.S. Joists 150 x 150mm / Rail poles | Elect | Labour | SWR10523 | 107 | EA | 5564 | 5564 | 0
30 | 52 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 58864 | 58864 | 0
31 | 17.5 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Elect | Labour | SWR10206 | 221 | TO | 3867.5 | 3867.5 | 0
32 | 17.5 | Un Loading of M.S.Channels, Angles, Flats & Rods etc., | Elect | Labour | SWR10524 | 185 | TO | 3237.5 | 3237.5 | 0
33 | 36.22 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel,iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading )-Above 10 KM and upto 20 KM | Elect | Labour | SWR10132 | 412.08 | TO | 14925.5376 | 14925.54 | -0.0024
34 | 68.44 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 450266.76 | 450266.76 | 0
35 | 60.008 | Plastering 2 Coats,20/16mm(1:6)(1:4) | Elect | Labour | SWR10862 | 373 | M2 | 22382.984 | 22382.98 | 0.004
36 | 8.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.-Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 18538.5 | 18538.5 | 0
37 | 8.5 | Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 7233.5 | 7233.5 | 0
38 | 52 | Painting suppports of 0.3m with bitumen | Elect | Labour | SWR10880 | 688 | EA | 35776 | 35776 | 0
39 | 8 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-8.0 m long PSCC pole | Elect | Labour | SWR10342 | 1500 | EA | 12000 | 12000 | 0
40 | 500 | Supply of rail poles 90/105lb (250x2N) | Elect | Supply | SMR22718 | 47.27 | KG | 23635 | 23635 | 0
41 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Rail pole 90 lbs | Elect | Labour | SWR10344 | 3510 | EA | 14040 | 14040 | 0
42 | 20 | Laying of XLPE UG Single Run cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders /Normal soil / CC/BT Road-33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11918 | 572.1 | M | 11442 | 11442 | 0
43 | 27.72 | Alligning the Main and Auxiliary structures such as RS joist,M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Elect | Labour | SWR10867 | 1470 | TO | 40748.4 | 40748.4 | 0
44 | 27.72 | Fabrication of Main and Auxiliary structures with power drillingusing raw steel such as M.S.Angles, Plates, Channels,R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site,including erection. | Elect | Labour | SWR10868 | 6852 | TO | 189937.44 | 189937.44 | 0
45 | 27.72 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.-Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 60457.32 | 60457.32 | 0
46 | 27.72 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.-Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium | Elect | Labour | SWR10879 | 482 | TO | 13361.04 | 13361.04 | 0
47 | 27.72 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete-Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elect | Supply | SMR40010 | 1293 | TO | 35841.96 | 35841.96 | 0
48 | 27.72 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete-Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 23589.72 | 23589.72 | 0
49 | 500 | Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions | Elect | Supply | SWR10873 | 83 | KG | 41500 | 41500 | 0
50 | 42 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | Elect | Supply | SMR11915 | 2055 | SET | 86310 | 86310 | 0
51 | 8 | Supply of Tension clamps for earth wire 3 bolted (Bus Stringing) | Elect | Supply | SMR40017 | 715 | SET | 5720 | 5720 | 0
52 | 24 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts &Bolts includng spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961)-Supply of I Bolts | Elect | Supply | SMR22473 | 294 | EA | 7056 | 7056 | 0
53 | 90 | Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nutswith spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . | Elect | Supply | SMR40011 | 299 | EA | 26910 | 26910 | 0
54 | 60 | Supply of CT stud clamps with hot dip galvanised bolts and nuts suitable for zebra / Panther conductor on one side and 28/30/40 mm CT stud on other side with stud size for single zebra / panther (4 bolted) with bimetallic sleeve for carrying 800 A | Elect | Supply | SMR40023 | 399 | EA | 23940 | 23940 | 0
55 | 31 | Supply of Alluminum alloy Pad clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for twin panther ACSR/Zebra of pad size 100 X 100 X15mm for carrying 1200 A current rating . | Elect | Supply | SMR40021 | 284 | EA | 8804 | 8804 | 0
56 | 12 | Supply of Alluminum PT clamps conforming to A6 of IS 617,with hot dip galvanised bolts and nuts suitable for single zebra/ Panther | Elect | Supply | SMR40025 | 368 | EA | 4416 | 4416 | 0
57 | 36 | Supply of Alluminum LA clamps conforming to A6 of IS 617, with hot dip galvanised bolts and nuts suitable for single zebra / Panther | Elect | Supply | SMR40027 | 357 | EA | 12852 | 12852 | 0
58 | 9 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 4.5mt) | Elect | Labour | SWR21240 | 781 | EA | 7029 | 7029 | 0
59 | 12 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Elect | Labour | SWR21241 | 507 | EA | 6084 | 6084 | 0
60 | 60 | Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Elect | Labour | SWR10884 | 224 | EA | 13440 | 13440 | 0
61 | 133.3 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | Elect | Labour | SWR10404 | 327.68 | M | 43679.744 | 43679.74 | 0.004
62 | 303 | Labour for Fixing of all types of clamps | Elect | Labour | SWR10917 | 65 | EA | 19695 | 19695 | 0
63 | 13 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 4500 | EA | 58500 | 58500 | 0
64 | 21 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR10393 | 3200 | EA | 67200 | 67200 | 0
65 | 1 | Erection of control/Relay panels, AC Panels, announciation panels etc in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Elect | Labour | SWR11893 | 2122 | EA | 2122 | 2122 | 0
66 | 35 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.-Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 4970 | 4970 | 0
67 | 64.584 | Excavate-Pit for 33KV VCB | Elect | Labour | SWR23224 | 331 | M3 | 21377.304 | 21377.3 | 0.004
68 | 74.52 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x1.8 x 0.75 cum for VCB Plinth | Elect | Labour | SWR20685 | 5160 | M3 | 384523.2 | 384523.2 | 0
69 | 2 | Erection of 33 KV VCB with Control Panel | Elect | Labour | SWR10460 | 12500 | EA | 25000 | 25000 | 0
70 | 10 | Erection of 11 KV VCB with Control Panel | Elect | Labour | SWR10461 | 12000 | EA | 120000 | 120000 | 0
71 | 16 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M(2.6" x 2.6" x 6.0") | Elect | Labour | SWR11039 | 928 | EA | 14848 | 14848 | 0
72 | 4 | Supply of Copper Flexible jumper with 75 X 8 of length 250mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral | Elect | Supply | SMR40033 | 4725 | EA | 18900 | 18900 | 0
73 | 12 | Supply of Bimetalic Copper die clamps suitable for power transformer/ Lclamps HV of 1/2 inch bush rod and other end suitable for panther conductor and with bimetallic sheet on the pad of size 75X75X10mm with four holes of 14mm diameter (hole to hole distance 40mm) with suitable GI bolts and nuts including washers | Elect | Supply | SMR40039 | 909 | EA | 10908 | 10908 | 0
74 | 4 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | SET | 3520 | 3520 | 0
75 | 2 | Erection of 11 KV LAS station type including earthing | Elect | Labour | SWR10397 | 559 | SET | 1118 | 1118 | 0
76 | 8 | Erection of 11 KV LAS line type including earthing | Elect | Labour | SWR10398 | 505 | SET | 4040 | 4040 | 0
77 | 34 | Providing of earthing with various types of earth electrodes-Supply of copper bonded steel rod of dia 5/8 inch with a length of 3meters, suitable for connecting 75X8 MS strip and supply of 33.9kgs ground enhancing meterial GEM-25A /Zerolyte of 0.2 ohm meter resistiviity as per IEE 142-1991 for 33/11kV Sub-Station | Elect | Supply | SMR40042 | 8820 | EA | 299880 | 299880 | 0
78 | 34 | Installation of copper bonded steel rod of dia 5/8 inch with a length of 3meters refilling with ground enhancing meterial EM- 25A / Zerolyte of 0.2 ohm meter resistiviity IEE 142-1992 in Hard Rock with bore 10"dia & 20feet deep or trench of 4'W X10'L X 5' depth back filled with black cotton soil | Elect | Labour | SWR10928 | 8004 | EA | 272136 | 272136 | 0
79 | 34 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elect | Labour | SWR10359 | 386 | EA | 13124 | 13124 | 0
80 | 1800 | Fabrication and connecting to risers from earth mat to structures, equipment,marshalling boxes, electrical panels, PLCC panels, fencing posts etc-M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Elect | Labour | SWR10919 | 41 | RMT | 73800 | 73800 | 0
81 | 957.45 | Laying of earth mat including excavation of trenches of depth 600mm, welding,connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication.-75x 8mm MS Flat / GI Flat. | Elect | Labour | SWR10920 | 65 | RMT | 62234.25 | 62234.25 | 0
82 | 2500 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends | Elect | Labour | SWR11879 | 27 | M | 67500 | 67500 | 0
83 | 270 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Elect | Labour | SWR12510 | 27 | EA | 7290 | 7290 | 0
84 | 1 | Erection of 220 V, 80 AH battery in complete shape fit for charging . VRLA(maintenance free) | Elect | Labour | SWR12344 | 2783 | EA | 2783 | 2783 | 0
85 | 1 | Erection of 220 V, 80 AH battery charger with Distribution board. | Elect | Labour | SWR12346 | 2783 | EA | 2783 | 2783 | 0
86 | 1 | Loading of 220V Battery set | Elect | Labour | SWR12083 | 900 | EA | 900 | 900 | 0
87 | 1 | Un-Loading of 220V Battery set | Elect | Labour | SWR12084 | 900 | EA | 900 | 900 | 0
88 | 1 | Loading of 220V Charger | Elect | Labour | SWR11244 | 572 | EA | 572 | 572 | 0
89 | 1 | Un-Loading of 220V Charger | Elect | Labour | SWR11245 | 366 | EA | 366 | 366 | 0
90 | 90 | Providing of control cable trench as per DATA-XII | Elect | Labour | SWR22093 | 3148 | RMT | 283320 | 283320 | 0
91 | 1 | Construction of DTR Plinth- RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | Elect | Labour | SWR21843 | 25967.57 | EA | 25967.57 | 25967.57 | 0
92 | 1 | Loading of 50,63, 75 & 100 KVA DTR | Elect | Labour | SWR10195 | 350 | EA | 350 | 350 | 0
93 | 1 | Un-Loading of 50,63, 75 & 100 KVA DTR | Elect | Labour | SWR10513 | 280 | EA | 280 | 280 | 0
94 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc-Erection of 3 Ph DTRs upto 25KVA | Elect | Labour | SWR10463 | 1139.95 | EA | 1139.95 | 1139.95 | 0
95 | 30 | Laying of XLPE UG Single Run cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable,placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders /Normal soil / CC/BT Road-11KV 3x185 Sqmm Cable | Elect | Labour | SWR11920 | 465.46 | M | 13963.8 | 13963.8 | 0
96 | 20 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x185 Sqmm Cable | Elect | Labour | SWR11956 | 126.23 | M | 2524.6 | 2524.6 | 0
97 | 2 | Making 11 KV 3x185 Sqmm Cable Out Door/Indoor end termination | Elect | Labour | SWR10390 | 2370.63 | EA | 4741.26 | 4741.26 | 0
98 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | Elect | Labour | SWR10674 | 1594.67 | EA | 1594.67 | 1594.67 | 0
99 | 1 | Supply of DC Annunciation & relay panel for 10 feeder panel including the cost of LED Indiacation lamps, VAA auxilairy relays, Electronic Hooters complete as per specification. | Elect | Supply | SMR40044 | 42500 | EA | 42500 | 42500 | 0
100 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. | Elect | Supply | SMR40045 | 42000 | EA | 42000 | 42000 | 0
101 | 2 | Fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supply | Elect | Labour | SWR20025 | 7871.85 | SET | 15743.7 | 15743.7 | 0
102 | 3 | Supply of FRP PT Marshalling Box | Elect | Supply | SMR40048 | 4463 | EA | 13389 | 13389 | 0
103 | 3 | Erection of Marshalling boxes | Elect | Labour | SWR10940 | 374.85 | EA | 1124.55 | 1124.55 | 0
104 | 2 | Erection of 33 KV single phase PTs | Elect | Labour | SWR10401 | 1079 | SET | 2158 | 2158 | 0
105 | 2 | Erection of 11 KV three phase PTs | Elect | Labour | SWR10402 | 800 | SET | 1600 | 1600 | 0
106 | 12 | Wirring, commissioning and testing of Outdoor Sub-station switchgear duly conducting the pre commissioning test as per relevent standards & issue of certificate by CEIG authorised testing Engineer | Elect | Labour | SWR10942 | 1825 | EA | 21900 | 21900 | 0
107 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading )-8MVA power transformer | Elect | Labour | SWR10854 | 21945 | EA | 43890 | 43890 | 0
108 | 2 | Loading of 8MVA PTR | Elect | Labour | SWR10613 | 5805.84 | EA | 11611.68 | 11611.68 | 0
109 | 2 | Un-Loading of 8MVA PTR | Elect | Labour | SWR10627 | 5805.84 | EA | 11611.68 | 11611.68 | 0
110 | 2 | Erection of PTR on constructed plinth-Erection of 8 MVA PTR. | Elect | Labour | SWR21321 | 49480.2 | EA | 98960.4 | 98960.4 | 0
111 | 2 | Testing of Power Transformer duly conducting the pre commissioning tests as per relevent standard & issue of certificate by CEIG authorised testing Engineer | Elect | Labour | SWR10944 | 4000 | EA | 8000 | 8000 | 0
112 | 2 | Loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10198 | 1024 | EA | 2048 | 2048 | 0
113 | 2 | Un-Loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10516 | 1044.48 | EA | 2088.96 | 2088.96 | 0
114 | 10 | Loading of 11 KV VCBs along with Panel boards | Elect | Labour | SWR10199 | 1024 | EA | 10240 | 10240 | 0
115 | 10 | Un-Loading of 11 KV VCBs along with Panel boards | Elect | Labour | SWR10517 | 1044.48 | EA | 10444.8 | 10444.8 | 0
116 | 75 | Supply of earthing pipe with materials GI Flat 25X3 mm | Elect | Supply | SMR11485 | 105 | KG | 7875 | 7875 | 0
117 | 90 | Laying of XLPE UG Single Run cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable,placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.- In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders /Normal soil / CC/BT Road-LT 3 1/2 x 185 Sqmm Cable | Elect | Labour | SWR11923 | 377.63 | M | 33986.7 | 33986.7 | 0
118 | 10 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-LT 3 1/2 x 185 Sqmm Cable | Elect | Labour | SWR11959 | 85.43 | M | 854.3 | 854.3 | 0
119 | 2 | Supply of 31/2x185Sqmm UG O/D end termination kits Making of Outdoor/Indoor End Termination | Elect | Supply | SMR40140 | 550 | EA | 1100 | 1100 | 0
120 | 1 | Loading of 11 KV HG Fuse Sets | Elect | Labour | SWR10231 | 18 | EA | 18 | 18 | 0
121 | 1 | Un Loading of 11 KV HG Fuse Sets | Elect | Labour | SWR10549 | 18 | EA | 18 | 18 | 0
122 | 1 | Erection of 11 KV HG Fuse set including earthing | Elect | Labour | SWR10395 | 740.52 | SET | 740.52 | 740.52 | 0
123 | 2 | Supply & fixing of Oout Door/Indoor end termination LT 3 1/2 x185 Sqmm Cable | Elect | Labour | SWR10765 | 968.9 | EA | 1937.8 | 1937.8 | 0
124 | 1 | Loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10238 | 80 | EA | 80 | 80 | 0
125 | 1 | Un Loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10556 | 80 | EA | 80 | 80 | 0
126 | 1 | Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR20102 | 1813.49 | EA | 1813.49 | 1813.49 | 0
127 | 3 | Supply of 11kv, 200Amps copper Flexible jumpers | Elect | Supply | SMR40032 | 131 | EA | 393 | 393 | 0
128 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard | Elect | Labour | SWR20032 | 1654 | EA | 1654 | 1654 | 0
129 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Elect | Labour | SWR22090 | 2205 | EA | 2205 | 2205 | 0
130 | 1 | T & P - Supply of -Wall clock standard make | Elect | Supply | SMR40059 | 578 | EA | 578 | 578 | 0
131 | 1 | Supply of Angle racks(18x36.6inches) Godrej | Elect | Supply | SMR40060 | 1733 | EA | 1733 | 1733 | 0
132 | 1 | Supply of 10ft Aluminium Ladder | Elect | Supply | SMR12378 | 1654 | EA | 1654 | 1654 | 0
133 | 30 | Painting of Name Plates for any equipment | Elect | Labour | SWR10963 | 122 | EA | 3660 | 3660 | 0
134 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7,8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19,20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378- 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579- 1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. | Elect | Supply | SMR40063 | 4925 | SET | 4925 | 4925 | 0
135 | 1 | Supply of Rechargeable LED torch light of Standard make | Elect | Supply | SMR40064 | 1733 | EA | 1733 | 1733 | 0
136 | 1 | Supply of Steel almarah(61/2 X 3ft) Godrej | Elect | Supply | SMR40061 | 9818 | EA | 9818 | 9818 | 0
137 | 1 | Supply of Table (3x6ft) Godrej | Elect | Supply | SMR40057 | 6050 | EA | 6050 | 6050 | 0
138 | 4 | Supply of S type chairs (Godrej) | Elect | Supply | SMR40058 | 924 | EA | 3696 | 3696 | 0
139 | 1 | Supply of Hack saw (12 inches) | Elect | Supply | SMR40065 | 289 | EA | 289 | 289 | 0
140 | 4 | Supply of Earth Rods (8ft) Screw & clamp type | Elect | Supply | SMR40066 | 578 | EA | 2312 | 2312 | 0
141 | 2 | Supply of Hand Gloves | Elect | Supply | SMR40067 | 289 | SET | 578 | 578 | 0
142 | 15 | Supply of Rubber mats ( 6’x3’) size for indoor SS | Elect | Supply | SMR40068 | 1386 | EA | 20790 | 20790 | 0
143 | 1 | Supply of Standard basic cell phone with charger | Elect | Supply | SMR40069 | 1386 | EA | 1386 | 1386 | 0
144 | 14 | Supply of Danger boards with clamps | Elect | Supply | SMR40070 | 116 | EA | 1624 | 1624 | 0
145 | 1 | Supply of Fire bucket stand with 3 buckets (8 -10 ltr capacity) | Elect | Supply | SMR40088 | 1386 | SET | 1386 | 1386 | 0
146 | 2 | Supply of Room fire extinguisher (2 ltrs capacity) for control room | Elect | Supply | SMR40089 | 4620 | EA | 9240 | 9240 | 0
147 | 4 | Supply of Trolley mounted CO2 (6.5Kgs) | Elect | Supply | SMR40087 | 9240 | EA | 36960 | 36960 | 0
148 | 6 | Supply of Safety Helmets of standard make | Elect | Supply | SMR40071 | 231 | EA | 1386 | 1386 | 0
149 | 8 | Supply of LC Boards | Elect | Supply | SMR40072 | 116 | EA | 928 | 928 | 0
150 | 4 | Supply of Gum Boots (Pair) | Elect | Supply | SMR40073 | 693 | EA | 2772 | 2772 | 0
151 | 1 | Supply of 5000v megger | Elect | Supply | SMR40074 | 13860 | EA | 13860 | 13860 | 0
152 | 1 | Supply of Earth megger (1000v) | Elect | Supply | SMR40075 | 8085 | EA | 8085 | 8085 | 0
153 | 1 | Supply of Digital clamp meter | Elect | Supply | SMR40076 | 2888 | EA | 2888 | 2888 | 0
154 | 1 | Supply of Name board of the 33/11kV Sub-Station(As per Standard Specification) | Elect | Supply | SMR40086 | 10238 | EA | 10238 | 10238 | 0
155 | 0.1 | Supply of Extention of 33KV Bay at 132/33KV Sub-station-Zebra condutor | Elect | Supply | SMR24910 | 299369 | KM | 29936.9 | 29936.9 | 0
156 | 8 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)-8 Mtrs long PSCC Poles | Elect | Labour | SWR20307 | 271.52 | EA | 2172.16 | 2172.16 | 0
157 | 7.04 | Earth work excavation of in all soils except hard rock requiring blasting. | Elect | Labour | SWR20768 | 345 | M3 | 2428.8 | 2428.8 | 0
158 | 7.04 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 46316.16 | 46316.16 | 0
159 | 6 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 19798.2 | 19798.2 | 0
160 | 13 | Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10239 | 126 | EA | 1638 | 1638 | 0
161 | 13 | Un Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10557 | 79 | EA | 1027 | 1027 | 0
162 | 21 | Loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10238 | 80 | EA | 1680 | 1680 | 0
163 | 21 | Un Loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10556 | 80 | EA | 1680 | 1680 | 0
164 | 2.604 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 10137.372 | 10137.37 | 0.002
165 | 35 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 5132.05 | 5132.05 | 0
166 | 16.912 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. | Elect | Labour | SWR10356 | 6579 | M3 | 111264.048 | 111264.05 | -0.002
167 | 6 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 6144 | 6144 | 0 | 4601055.4996
168 | 6 | Un Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 6144 | 6144 | 0
169 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 13198.8 | 13198.8 | 0
170 | 400 | Laying of XLPE UG cable Triple or more Run including excavation of trench of size 1000mm wide to 750mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs &33 KV - 1.20 mtrs.Along the CC / BT multi layer road requiring compressor-33 KV 3x400 Sqmm Cable | Elect | Labour | SWR12019 | 1731.45 | M | 692580 | 692580 | 0
171 | 100 | Laying of XLPE UG cable Triple or more Run including excavation of trench of size 1000mm wide to 750mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs &33 KV - 1.20 mtrs.Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe)-33 KV 3x400 Sqmm Cable | Elect | Labour | SWR12024 | 1978.8 | M | 197880 | 197880 | 0
172 | 1000 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 204.1 | M | 204100 | 204100 | 0
173 | 150 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11954 | 135.66 | M | 20349 | 20349 | 0
174 | 14 | Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination | Elect | Labour | SWR10387 | 2764.76 | EA | 38706.64 | 38706.64 | 0
175 | 6 | Making of Straight through joints-33 KV 3x400 Sqmm Cable | Elect | Labour | SWR10382 | 5700.78 | EA | 34204.68 | 34204.68 | 0
176 | 50 | Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | Elect | Supply | SMR40077 | 363 | M | 18150 | 18150 | 0
177 | 970 | Supply of 6" B class GI pipe Cost of Pipes and slabs | Elect | Supply | SMR40081 | 1044 | M | 1012680 | 1012680 | 0
178 | 50 | supply of 6" DWC pipe Cost of Pipes and slabs | Elect | Supply | SMR11610 | 1012 | M | 50600 | 50600 | 0
179 | 500 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours.-11KV | Elect | Labour | SWR21903 | 30 | M | 15000 | 15000 | 0
180 | 2 | Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10239 | 126 | EA | 252 | 252 | 0
181 | 2 | Un Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10557 | 79 | EA | 158 | 158 | 0
182 | 2 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 4500 | EA | 9000 | 9000 | 0
183 | 3 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elect | Supply | SMR11482 | 3486 | EA | 10458 | 10458 | 0
184 | 3 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 3702.6 | 3702.6 | 0
185 | 3 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elect | Labour | SWR10359 | 386 | EA | 1158 | 1158 | 0
186 | 2 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 293.26 | 293.26 | 0
187 | 0.186 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3893.01 | M3 | 724.0999 | 724.1 | -0.00014
188 | 12 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 6150.6 | 6150.6 | 0
189 | 6 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 15862.98 | 15862.98 | 0
190 | 12 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 912 | 912 | 0
191 | 12 | Un-Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 600 | 600 | 0
192 | 6 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 6792 | 6792 | 0
193 | 6.3 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 41447.7 | 41447.7 | 0
194 | 6 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | Elect | Labour | SWR10107 | 700 | EA | 4200 | 4200 | 0
195 | 7.17 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Elect | Labour | SWR10206 | 221 | TO | 1584.57 | 1584.57 | 0
196 | 7.17 | Un Loading of M.S.Channels, Angles, Flats & Rods etc., | Elect | Labour | SWR10524 | 185 | TO | 1326.45 | 1326.45 | 0
197 | 10.17 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel,iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading )-Above 10 KM and upto 20 KM | Elect | Labour | SWR10132 | 412.08 | TO | 4190.8536 | 4190.85 | 0.0036
198 | 30 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)-Trans 11/12.5/12.9M Spun pole upto 50KM | Elect | Labour | SWR11181 | 858 | EA | 25740 | 25740 | 0
199 | 30 | Loading of Spun poles 12.5 M | Elect | Labour | SWR10190 | 548 | EA | 16440 | 16440 | 0
200 | 30 | Un loading of Spun poles 12.5 M | Elect | Labour | SWR10508 | 363 | EA | 10890 | 10890 | 0
201 | 30 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Spun poles 12.5 Mtrs / 12.9Mtrs PSCC | Elect | Labour | SWR10350 | 4521.66 | EA | 135649.8 | 135649.8 | 0
202 | 15 | Excavation of pits in all soils except hard rock requiring blasting-12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") 1.94 cum | Elect | Labour | SWR10109 | 842.78 | EA | 12641.7 | 12641.7 | 0
203 | 15 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") | Elect | Labour | SWR11041 | 1466.25 | EA | 21993.75 | 21993.75 | 0
204 | 58.4 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 384213.6 | 384213.6 | 0
205 | 6 | S&E-Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 16470 | 16470 | 0
206 | 1 | Submission of auto CAD Drawing as per pole schedule (Detailed survey and sketch)-Up to 10 km | Elect | Labour | SWR12104 | 6000 | LS | 6000 | 6000 | 0
207 | 1.2 | Paving out and stringing of conductor by providing temporary stays, tensioning,sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location-100 Sqmm Double Circuit (6 Conductors). | Elect | Labour | SWR10704 | 26255.98 | KM | 31507.176 | 31507.18 | -0.004
208 | 5 | Formation of Cut point for 33 KV Double circuit line excluding pole erection and stays | Elect | Labour | SWR10466 | 3198.72 | EA | 15993.6 | 15993.6 | 0
209 | 1.2 | Dismantling of 11KV 34/55 sqmm SC | Elect | Labour | SWR22065 | 4500 | KM | 5400 | 5400 | 0
210 | 1.2 | Restringing of existing loose Lines by removing the pin-binding and jumpers, Providing of temporary stays, providing stiffners pieces, replacement of damaged insulators, alignment of cross arms, pin binding and jumpering after tensioning and removing of the temporary stays complete-33/11 KV lines-Restringing of with 55 Sqmm single ckt 3 cond | Elect | Labour | SWR11308 | 6616 | KM | 7939.2 | 7939.2 | 0
211 | 1.2 | Restringing of existing loose Lines by removing the pin-binding and jumpers, Providing of temporary stays, providing stiffners pieces, replacement of damaged insulators, alignment of cross arms, pin binding and jumpering after tensioning and removing of the temporary stays complete-LT lines :-Restring. Of LT line 4w/l with 34 Sqmm | Elect | Labour | SWR11313 | 7270 | KM | 8724 | 8724 | 0
212 | 2 | Loading of Conductor drums | Elect | Labour | SWR10191 | 202 | EA | 404 | 404 | 0
213 | 2 | Un Loading of Conductor drums | Elect | Labour | SWR10509 | 100 | EA | 200 | 200 | 0
214 | 150 | Loading of 33 & 11 KV Disc insulators | Elect | Labour | SWR12416 | 2 | CRT | 300 | 300 | 0
215 | 150 | Un loading of 33 KV Pin insulators | Elect | Labour | SWR10529 | 3 | CRT | 450 | 450 | 0
216 | 60 | Loading of 33 & 11 KV Disc insulators | Elect | Labour | SWR12416 | 2 | CRT | 120 | 120 | 0
217 | 60 | Un Loading of 33 & 11 KV Disc insulators | Elect | Labour | SWR10631 | 2 | CRT | 120 | 120 | 0
218 | 3 | Loading of 33 KV Metal parts | Elect | Labour | SWR10618 | 65 | BAG | 195 | 195 | 0
219 | 3 | Un Loading of 33 KV Metal parts | Elect | Labour | SWR10632 | 65 | BAG | 195 | 195 | 0
220 | 75 | Supply of earthing pipe with materials-Supply of GI wire No 8 | Elect | Supply | SMR11486 | 105 | KG | 7875 | 7875 | 0
221 | 5 | Earthing of Sub-Station- Supply of GI pipe 40 mm dia, 2 mtrs, 3mm thickness with bolts and nuts | Elect | Supply | SMR40091 | 733 | EA | 3665 | 3665 | 0
222 | 5 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 6171 | 6171 | 0
223 | 7000 | Cut-Tree Branch(LT/11/33)&Trnsprt Debris | Elect | Labour | SWR23200 | 4 | EA | 28000 | 28000 | 0
224 | 1750 | Supply of earthing pipe with materials-Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 205625 | 205625 | 0
225 | 10 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 4840 | 4840 | 0
226 | 150 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Elect | Labour | SWR11879 | 27 | M | 4050 | 4050 | 0
227 | 12 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properlyramming including transport of materials from road side to location excluding pit excavation-11 Mtrs PSCC poles | Elect | Labour | SWR10978 | 4336.85 | EA | 52042.2 | 52042.2 | 0
228 | 12 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)-11 Mtrs long PSCC Poles | Elect | Labour | SWR11180 | 431.97 | EA | 5183.64 | 5183.64 | 0
229 | 12 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | Elect | Labour | SWR10107 | 700 | EA | 8400 | 8400 | 0
230 | 15.79 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 103882.41 | 103882.41 | 0
231 | 3 | Supply of M+3 Tower (Galvanized) | Elect | Supply | SMR11683 | 140674.3 | EA | 422022.9 | 422022.9 | 0
232 | 3 | Erection of M+3 Tower (Galvanized) | Elect | Labour | SWR11850 | 64576 | EA | 193728 | 193728 | 0
233 | 6 | Supply of material for Extension of 3Mtrs for M+3 (Galvanized) | Elect | Supply | SMR11684 | 28520.64 | EA | 171123.84 | 171123.84 | 0
234 | 6 | Erection of Extension of 3Mtrs for M+3 (Galvanized) | Elect | Labour | SWR11851 | 5168.95 | EA | 31013.7 | 31013.7 | 0
235 | 14.256 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-M-Type Tower (1.2M x 1.2M x 3.3M ) 4.752cum | Elect | Labour | SWR12090 | 3592.95 | EA | 51221.0952 | 51221.1 | -0.0048
236 | 1.2 | Dismantling of 34/ 55 sqmm (2wire) | Elect | Labour | SWR12162 | 2000 | KM | 2400 | 2400 | 0
237 | 2 | Supply and Installation of 33KV indoor type Single VCB panel Switchboard (Schneider make ) including the cost of testing and commissioning | Elect | Labour | SWR25187 | 1300000 | EA | 2600000 | 2600000 | 0
238 | 90 | Fabrication of materials including 2 coats of Red oxide painting Back clamps with 75 x 8 mm MS Flat | Elect | Labour | SWR10319 | 31 | EA | 2790 | 2790 | 0
239 | 5 | Fabrication of materials including 2 coats of Red oxide painting Strut clamps with 75 x 8 mm MS Flat | Elect | Labour | SWR11262 | 84 | EA | 420 | 420 | 0
240 | 229.16 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Elect | Labour | SWR10919 | 41 | RMT | 9395.56 | 9395.56 | 0
241 | 7.62 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 26106.12 | 26106.12 | 0
242 | 6 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 6144 | 6144 | 0 | 7060092.5247
243 | 6 | Un Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 6144 | 6144 | 0
244 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators,transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)-Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 16498.5 | 16498.5 | 0
245 | 240 | Laying of XLPE UG cable Six Run including excavation of trench of size 1050mm wide to 1200mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.-Along the CC / BT multi layer road requiring compressor-11 KV 3x300 Sqmm Cable | Elect | Labour | SWR12070 | 2173.88 | M | 521731.2 | 521731.2 | 0
246 | 240 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of leadand lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts,-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders /Normal soil/CC-11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11973 | 631.06 | M | 151454.4 | 151454.4 | 0
247 | 200 | Laying of XLPE UG Single Run cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs-Along the CC / BT multi layer road requiring compressor-11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11928 | 1073.94 | M | 214788 | 214788 | 0
248 | 1440 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 204.1 | M | 293904 | 293904 | 0
249 | 160 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11955 | 144.08 | M | 23052.8 | 23052.8 | 0
250 | 20 | Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | Elect | Labour | SWR10391 | 2370.63 | EA | 47412.6 | 47412.6 | 0
251 | 7 | Making of Straight through joints-11 KV 3x300 Sqmm Cable | Elect | Labour | SWR10386 | 3725.45 | EA | 26078.15 | 26078.15 | 0
252 | 50 | Supply of 150 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | Elect | Supply | SMR40078 | 303 | M | 15150 | 15150 | 0
253 | 1400 | Supply of 4" B class GI pipe Cost of Pipes and slabs | Elect | Supply | SMR40080 | 740 | M | 1036000 | 1036000 | 0
254 | 50 | supply of 4" DWC pipe Cost of Pipes and slabs | Elect | Supply | SMR11609 | 759 | M | 37950 | 37950 | 0
255 | 440 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours.-11KV | Elect | Labour | SWR21903 | 30 | M | 13200 | 13200 | 0
256 | 8 | Loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10238 | 80 | EA | 640 | 640 | 0
257 | 8 | Un Loading of 11KV AB Switch Conventional type | Elect | Labour | SWR10556 | 80 | EA | 640 | 640 | 0
258 | 8 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR10393 | 3200 | EA | 25600 | 25600 | 0
259 | 35 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 43197 | 43197 | 0
260 | 35 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elect | Labour | SWR10359 | 386 | EA | 13510 | 13510 | 0
261 | 8 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 1173.04 | 1173.04 | 0
262 | 35 | Supply of GI eath pipe with 40 mm dia,3mm thcikness with 2.0M Length | Elect | Supply | SMR11480 | 698 | EA | 24430 | 24430 | 0
263 | 22 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 58164.26 | 58164.26 | 0
264 | 44 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 3344 | 3344 | 0
265 | 44 | Un-Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 2200 | 2200 | 0
266 | 22 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 24904 | 24904 | 0
267 | 22 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | Elect | Labour | SWR10107 | 700 | EA | 15400 | 15400 | 0
268 | 0.682 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 2655.026 | 2655.03 | -0.004
269 | 28.96 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 190527.84 | 190527.84 | 0
270 | 8.1 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Elect | Labour | SWR10206 | 221 | TO | 1790.1 | 1790.1 | 0
271 | 8.1 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Elect | Labour | SWR10524 | 185 | TO | 1498.5 | 1498.5 | 0
272 | 19.225 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel,iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading )-Above 10 KM and upto 20 KM | Elect | Labour | SWR10132 | 412.08 | TO | 7922.238 | 7922.24 | -0.002
273 | 10 | Loading of 11 KV AB Cable (XLPE) 3 Core upto 500 Mts. Drum (including Accessories ) | Elect | Labour | SWR12413 | 584 | DR | 5840 | 5840 | 0
274 | 10 | Un loading of 11 KV AB Cable (XLPE) 3 Core upto 500 Mts.Drum (including Accessories ) | Elect | Labour | SWR12431 | 438 | DR | 4380 | 4380 | 0
275 | 4.9 | Stringing of HT AB Cable with GI Metal Parts-HT AB Cable 11 KV 3x185+70 Sqmm | Elect | Labour | SWR10454 | 41876.1 | KM | 205192.89 | 205192.89 | 0
276 | 69 | Supply of 11KV 3x185+70sq.mm/ 3x70+70sq.mm/3x35+35sq.mm AB cable end Kits | Elect | Supply | SMR11504 | 950 | SET | 65550 | 65550 | 0
277 | 2000 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 235000 | 235000 | 0
278 | 300 | Drilling of holes upto 20 mm dia using power drills-MS Channel, Angles and flat | Elect | Labour | SWR10307 | 4 | EA | 1200 | 1200 | 0
279 | 100 | Cutting charges for MS Sections-MS Channel 100 x 50 mm | Elect | Labour | SWR10294 | 10 | EA | 1000 | 1000 | 0
280 | 76 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properlyramming including transport of materials from road side to location excluding pit excavation-11 Mtrs PSCC poles | Elect | Labour | SWR10978 | 4336.85 | EA | 329600.6 | 329600.6 | 0
281 | 76 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)-11 Mtrs long PSCC Poles | Elect | Labour | SWR11180 | 431.97 | EA | 32829.72 | 32829.72 | 0
282 | 76 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | Elect | Labour | SWR10107 | 700 | EA | 53200 | 53200 | 0
283 | 100.03 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 658097.37 | 658097.37 | 0
284 | 2 | Loading of Conductor drums | Elect | Labour | SWR10191 | 202 | EA | 404 | 404 | 0
285 | 2 | Un Loading of Conductor drums | Elect | Labour | SWR10509 | 100 | EA | 200 | 200 | 0
286 | 2 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)-Trans 11/12.5/12.9M Spun pole upto 50KM | Elect | Labour | SWR11181 | 858 | EA | 1716 | 1716 | 0
287 | 2 | Loading of Spun poles 12.5 M | Elect | Labour | SWR10190 | 548 | EA | 1096 | 1096 | 0
288 | 2 | Un Loading of Spun poles 12.5 M | Elect | Labour | SWR10508 | 363 | EA | 726 | 726 | 0
289 | 2 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Spun poles 12.5 Mtrs / 12.9Mtrs PSCC | Elect | Labour | SWR10350 | 4521.66 | EA | 9043.32 | 9043.32 | 0
290 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") | Elect | Labour | SWR11041 | 1466.25 | EA | 2932.5 | 2932.5 | 0
291 | 3.88 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 25526.52 | 25526.52 | 0
292 | 8 | S&E-Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 21960 | 21960 | 0
293 | 5000 | Cut-Tree Branch(LT/11/33)&Trnsprt Debris | Elect | Labour | SWR23200 | 4 | EA | 20000 | 20000 | 0
294 | 1.65 | Paving out and stringing of conductor by providing temporary stays, tensioning,sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location.-100 Sqmm Single Circuit (3 Conductors) | Elect | Labour | SWR10366 | 13856.7 | KM | 22863.555 | 22863.56 | -0.005
295 | 12 | Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays | Elect | Labour | SWR10653 | 1435.81 | EA | 17229.72 | 17229.72 | 0
296 | 138 | Loading of 11KV pin insulators/Post type insulators/ Solid core insulators | Elect | Labour | SWR10212 | 1 | CRT | 138 | 138 | 0
297 | 138 | Un Loading of 11KV pin insulators/Post type insulators/ Solid core insulators | Elect | Labour | SWR10530 | 1 | CRT | 138 | 138 | 0
298 | 72 | Loading of 33 & 11 KV Disc insulators | Elect | Labour | SWR12416 | 2 | CRT | 144 | 144 | 0
299 | 72 | Un Loading of 33 & 11 KV Disc insulators | Elect | Labour | SWR10631 | 2 | CRT | 144 | 144 | 0
300 | 2 | Loading of 11 KV Metal parts | Elect | Labour | SWR12402 | 48 | BAG | 96 | 96 | 0
301 | 2 | Un Loading of 11 KV Metal parts | Elect | Labour | SWR12421 | 48 | BAG | 96 | 96 | 0
302 | 46 | Loading of 11 KV V - Cross arms | Elect | Labour | SWR10228 | 4 | EA | 184 | 184 | 0
303 | 46 | Un Loading of 11 KV V - Cross arms | Elect | Labour | SWR10546 | 4 | EA | 184 | 184 | 0
304 | 1 | Transport of steel including line materials such as cross arms, clamps, hardware, cable (loose) and other line materials (Including loading and unloading)-Above 10 KM and upto 20 KM | Elect | Labour | SWR10148 | 481.44 | TO | 481.44 | 481.44 | 0
305 | 4.752 | Excavation of pits in all soils except hard rock requiring blasting-M-Type Tower (1.2M x 1.2M x 3.3M ) 4.752cum | Elect | Labour | SWR12085 | 1997.93 | EA | 9494.1634 | 9494.16 | 0.00336
306 | 9.504 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)-M-Type Tower (1.2M x 1.2M x 3.3M ) 4.752cum | Elect | Labour | SWR12090 | 3592.95 | EA | 34147.3968 | 34147.4 | -0.0032
307 | 2.9 | Dismantling of 11KV 34/55 sqmm SC | Elect | Labour | SWR22065 | 4500 | KM | 13050 | 13050 | 0
308 | 2.9 | Restringing of existing loose Lines by removing the pin-binding and jumpers, Providing of temporary stays, providing stiffners pieces, replacement of damaged insulators, alignment of cross arms, pin binding and jumpering after tensioning and removing of the temporary stays complete -Restringing of with 55 Sqmm single ckt 3 cond | Elect | Labour | SWR11308 | 6616 | KM | 19186.4 | 19186.4 | 0
309 | 3 | Supply of M+3 Tower (Galvanized) | Elect | Supply | SMR11683 | 140674.3 | EA | 422022.9 | 422022.9 | 0
310 | 3 | Erection of M+3 Tower (Galvanized) | Elect | Labour | SWR11850 | 64576 | EA | 193728 | 193728 | 0
311 | 6 | Supply of material for Extension of 3Mtrs for M+3 (Galvanized) | Elect | Supply | SMR11684 | 28520.64 | EA | 171123.84 | 171123.84 | 0
312 | 6 | Erection of Extension of 3Mtrs for M+3 (Galvanized) | Elect | Labour | SWR11851 | 5168.95 | EA | 31013.7 | 31013.7 | 0
313 | 12 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-9.1 M long PSCC pole | Elect | Labour | SWR10343 | 2400 | EA | 28800 | 28800 | 0
314 | 12 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)-9.1 Mtrs long PSCC Poles | Elect | Labour | SWR20308 | 407.29 | EA | 4887.48 | 4887.48 | 0
315 | 88 | Loading of PSCC Poles 9.1 M | Elect | Labour | SWR10188 | 182 | EA | 16016 | 16016 | 0
316 | 88 | Un Loading of PSCC Poles 9.1 M | Elect | Labour | SWR10506 | 91 | EA | 8008 | 8008 | 0
317 | 12 | Excavation of pits in all soils except hard rock requiring blasting-9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | Elect | Labour | SWR10107 | 700 | EA | 8400 | 8400 | 0
318 | 23.36 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 153685.44 | 153685.44 | 0
319 | 44 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 22552.2
320 | 69 | End Termination of AB cable (each lead):120 Sqmm to 185 Sqmm | Elect | Labour | SWR10667 | 800 | EA | 55200
321 | 124 | Straight through joints of AB cable (each lead) Supply and ere Straight line Asmbly kits | Elect | Labour | SWR10672 | 1661 | EA | 205964
322 | 34 | Straight through joints of AB cable (each lead) Supply and ere Angle line Asmbly kits | Elect | Labour | SWR10673 | 2124 | EA | 72216
323 | 48 | Erection of Assemble Kit for 'T' Branche | Elect | Labour | SWR10671 | 1800 | EA | 86400
324 | 48 | Supply and erection of T-Branch kit | Elect | Supply | SWR24971 | 3215 | EA | 154320 | 6254512.8092
| Sub Total: | [6 empty] | 18793497.3234
| 18% Service tax on labour | [6 empty] | 3382829.5182
| Total Rs. | [6 empty] | 22176326.8416 | 22176326.85 | 0.0083644
313 | 28 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Box pole 12 Mtr | Elect | Labour | SWR11267 | 3901.37 | EA | 109238.36 | 28800 | 80438.36
1035847.0582
|  |  |  | 4982522.3172 |  | 1890504.1528 |  |  |  | 22176326.8494
6751163.9602
7516289.3532
20285822.6888

## Sandhya Hotels SS new (hidden)
SCHEDULE
Name of the Work : Erection of 33/11KV Indoor Substation with 2Nos. 12.5 MVA Power Transformers at SANDHYA HOTELS Opp Sunshine Hospitals Raidurgam under T&D Improvement Works.
WBS Element : S-1547-12-01-03-01-001
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 6 | Supply 9mtrs tubular poles single way | Elect | Labour | SMR40051 | 13913 | EA | 83478
2 | 6 | Errection of tubular poles | Elect | Labour | SWR10955 | 1379 | EA | 8274
3 | 2 | SupCU Flexi jumper for Power T/F Neutral | Elect | Labour | SMR40033 | 4725 | EA | 9450
4 | 1 | LOADING of 50,63,75&100kva DTR | Elect | Labour | SWR10195 | 349.65 | EA | 349.65
5 | 1 | UNLOADING of 50,63,75&100kva DTR | Elect | Labour | SWR10513 | 280.35 | EA | 280.35
6 | 1 | Erection of Three Phase DTRs | Elect | Labour | SWR10463 | 1525 | EA | 1525
7 | 1 | Contruction of DTR column at 33/11kV SS | Elect | Labour | SWR23010 | 7235 | EA | 7235
8 | 1 | Erection of LT distribution box | Elect | Labour | SWR10674 | 1242 | EA | 1242
9 | 2600 | Laying contl cable10x2.5 Sqmm Cu cable | Elect | Labour | SWR11879 | 14 | M | 36400
10 | 1 | Supply of AC Supply panel complete | Elect | Labour | SMR40045 | 42000 | EA | 42000
11 | 1 | Erecction of AC/ DC control panel complete | Elect | Labour | SWR11893 | 2122 | EA | 2122
12 | 10 | LOADING of 33 KV VCBs&Panel boards | Elect | Labour | SWR10198 | 1024 | EA | 10240
13 | 10 | UN-LOADING of 33 KV VCBs&Panel boards | Elect | Labour | SWR10516 | 1024 | EA | 10240
14 | 10 | TRANSPORT OF COND DRUM,VCBs upto 10km | Elect | Labour | SWR11860 | 2667 | EA | 26670
15 | 10 | Erection of 33KV indoor switchgear panel | Elect | Labour | SWR10930 | 8990 | EA | 89900
16 | 750 | Supply,fabricati of 6mm Checkerd plates | Elect | Labour | SWR10873 | 83 | KG | 62250
17 | 12 | SupRubber mats( 6#x3#)size for indoorSS | Elect | Labour | SMR40068 | 1386 | EA | 16632
18 | 1 | Sup Alluminium Ladder for indoor works | Elect | Labour | SMR12378 | 1654 | EA | 1654
19 | 2 | Sup TrollyMounted Co2 Cylinders(IS-2878) | Elect | Labour | SMR40087 | 9240 | EA | 18480
20 | 2 | Sup Fire Buckets Stand with Buckets | Elect | Labour | SMR40088 | 1386 | SET | 2772
21 | 6 | Sup Fire Extinguisher for Control Room | Elect | Labour | SMR40089 | 4620 | EA | 27720
22 | 4 | Supply of Safety Helmet of standard make | Elect | Labour | SMR40071 | 231 | EA | 924
23 | 4 | Sup Earth Rods (8ft) Screw & clamp type | Elect | Labour | SMR40066 | 578 | EA | 2312
24 | 4 | Supply of Hand Gloves | Elect | Labour | SMR40067 | 289 | SET | 1156
25 | 1 | Sup Stand basic cell phone with charger | Elect | Labour | SMR40069 | 1386 | EA | 1386
26 | 1 | Sup Steel almarah(61/2 X 3ft) Godrej | Elect | Labour | SMR40061 | 9818 | EA | 9818
27 | 1 | Supply of Table (3x6ft) Godrej | Elect | Labour | SMR40057 | 6050 | EA | 6050
28 | 4 | Supply of S type chairs (Godrej) | Elect | Labour | SMR40058 | 924 | EA | 3696
29 | 1 | Sup Angle racks(18x36.6inches) Godrej | Elect | Labour | SMR40060 | 1733 | EA | 1733
30 | 10 | Supply of Danger boards with clamps | Elect | Labour | SMR40070 | 116 | EA | 1160
31 | 1 | Sup 33/11kv S.S Permanent name board | Elect | Labour | SMR40086 | 10238 | EA | 10238
32 | 1 | Supply of Wall clock standard make | Elect | Labour | SMR40059 | 578 | EA | 578
33 | 1 | SupTaparia Tool kit complete as per Spec | Elect | Labour | SMR40063 | 4925 | SET | 4925
34 | 2 | Sup Rechargeable LED torch light. | Elect | Labour | SMR40064 | 1733 | EA | 3466
35 | 1 | Supply of Hack saw (12 inches) | Elect | Labour | SMR40065 | 289 | EA | 289
36 | 8 | Supply of LC Boards | Elect | Labour | SMR40072 | 116 | EA | 928
37 | 2 | Supply of Gum Boots | Elect | Labour | SMR40073 | 693 | EA | 1386
38 | 1 | Supply of Digital clamp meter. | Elect | Labour | SMR40076 | 2888 | EA | 2888
39 | 1 | Supply of 5000v megger | Elect | Supply | SMR40074 | 13860 | EA | 13860
40 | 1 | Sup &fix of board ind Switchyard layout | Elect | Labour | SWR20032 | 1654 | EA | 1654
41 | 1 | Sup& fix safety inst/SS Op. inst board | Elect | Supply | SWR22090 | 2205 | EA | 2205
42 | 6 | Supply of 150 W LED Fixture set | Elect | Labour | SMR23116 | 13500 | EA | 81000
43 | 36 | Supply of CI pipe of 100 mm dia 2.75 mtr | Elect | Labour | SMR11482 | 3486 | EA | 125496
44 | 2 | Supply of GI pipe of 40 mm dia 2 mtrs | Elect | Labour | SMR11480 | 698 | EA | 1396
45 | 8.8 | Earth work excav for founda lead&lifts | Elect | Supply | SWR10857 | 331 | M3 | 2912.8
46 | 90 | Laying of LT 185 S.Run AR in HG/NS/CC/BT | Elect | Labour | SWR11923 | 295 | M | 26550
47 | 10 | Raising of UG Cable LT 3 1/2 x 185 Sqmm | Elect | Supply | SWR11959 | 67 | M | 670
48 | 2 | sup of LT3.5x185sqmm od/id termination k | Elect | Labour | SMR40140 | 550 | EA | 1100
49 | 2 | OD/Idoor end termination LT 3 1/2 x 185 | Elect | Supply | SWR10765 | 809 | EA | 1618
50 | 50 | Laying of 11kV35 S.Run AR in HG/NS/CC/BT | Elect | Labour | SWR11922 | 339 | M | 16950
51 | 15 | Raising of UG Cable 11 KV 3x35 Sqmm 3 | Elect | Supply | SWR11958 | 87 | M | 1305
52 | 2 | OD/Idoor end termination 11kv 3x35 xlpe | Elect | Supply | SWR10388 | 1444 | EA | 2888
53 | 2 | Erection of RS Joist 150 x 150 mm | Elect | Supply | SWR10348 | 1407 | EA | 2814
54 | 4 | Erection of RS Joist 175 x 85 mm | Elect | Supply | SWR10346 | 1131.9 | EA | 4527.6
55 | 638.29 | Laying of earth mat,excavation 75x 8mm | Elect | Supply | SWR10920 | 65 | RMT | 41488.85
56 | 250 | Laying of Earth mat 50x6mm flat | Elect | Supply | SWR21170 | 65 | M | 16250
57 | 16 | LOADING of 11 KV VCBs&Panel boards | Elect | Supply | SWR10199 | 1024 | EA | 16384
58 | 16 | UNLOADING of 11 KV VCBs&Panel boards | Elect | Supply | SWR10517 | 1024 | EA | 16384
59 | 16 | Erection of 11KV indoor switchgear panel | Elect | Supply | SWR10931 | 7980 | EA | 127680
60 | 1 | LOADING of 11 KV AB SWCH T.T.200/400 A | Elect | Supply | SWR10238 | 80 | EA | 80
61 | 1 | UNLOADING of 11 KV AB SWCH T.T.200/400 A | Elect | Supply | SWR10556 | 80 | EA | 80
62 | 1 | Erection of 11kv ABSwitch incl earthing | Elect | Supply | SWR10393 | 1598.34 | EA | 1598.34
63 | 1 | LOADING of 11 KV HG Fuse Sets | Elect | Supply | SWR10231 | 18 | EA | 18
64 | 1 | UNLOADING of 11 KV HG Fuse Sets | Elect | Supply | SWR10549 | 18 | EA | 18
65 | 1 | Erect. of 11kv HG Fuseset incl earthing | Elect | Supply | SWR10395 | 660 | SET | 660
66 | 500 | Cable terminations to the switchgear | Elect | Supply | SWR20813 | 27 | LS | 13500
67 | 1 | Loading 220 V Battery with Charger | Elect | Supply | SWR11166 | 1612 | SET | 1612
68 | 1 | Un-loading 220 V Battery with Charger | Elect | Supply | SWR11147 | 1024 | SET | 1024
69 | 1 | Erec 220V Battery with charger incl eart | Elect | Supply | SWR11772 | 5053 | EA | 5053
70 | 2 | Fab & laying of ladder in cable trench | Elect | Supply | SWR22088 | 788 | EA | 1576
71 | 6 | Fixing of LED/Metal halide complete. | Elect | Supply | SWR10956 | 1268 | EA | 7608
72 | 3.35 | Sup Material for 1st coat Al. Painting. | Elect | Supply | SMR40009 | 2181 | TO | 7306.35
73 | 9 | Painting suppports of 0.3m with bitumen | Elect | Supply | SWR10880 | 688 | EA | 6192
74 | 1 | Painting AB switch OP rods with PO red | Elect | Supply | SWR10881 | 142 | EA | 142
75 | 2 | Transport of 12.5MVA power transformer | Elect | Supply | SWR10855 | 27431 | EA | 54862
76 | 2 | LOADING of 12.5 MVA PTR | Elect | Supply | SWR10614 | 12128 | EA | 24256
77 | 2 | UNLOADING of 12.5 MVA PTR | Elect | Supply | SWR10628 | 12128 | EA | 24256
78 | 2 | Erection of 12.5 MVA PTR. | Elect | Labour | SWR10929 | 51818 | EA | 103636
79 | 36 | Errection of CI Earth pit as per IS3043 | Elect | Labour | SWR10923 | 2122 | EA | 76392
80 | 2 | Provd earthing with pit incl. GI pipe | Elect | Supply | SWR20182 | 1048 | EA | 2096
81 | 16 | TRANSPORT OF COND DRUM,VCBs upto 10km | Elect | Labour | SWR11860 | 2667 | EA | 42672
82 | 3.35 | Fabrication of struc.with power drilling | Elect | Labour | SWR10868 | 6852 | TO | 22954.2
83 | 9 | Fabrication of 175x85/150x75mm RS joist | Elect | Supply | SWR10642 | 402 | EA | 3618
84 | 12 | Fixing of 90lb rail poles for T/F | Elect | Labour | SWR11008 | 403 | RMT | 4836
85 | 3.35 | Sup Material for 2nd coat Al. Painting. | Elect | Labour | SMR40010 | 1293 | TO | 4331.55
86 | 3.35 | Labour for 1st coat Al. Painting. | Elect | Labour | SWR10877 | 851 | TO | 2850.85
87 | 3.35 | Labour for 2nd coat Al. Painting. | Elect | Labour | SWR10879 | 482 | TO | 1614.7
88 | 22 | Line//Load-33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 22528
89 | 22 | Unload-33KV XLPE UG Cable all sizes | Elect | Labour | SWR11231 | 1024 | DR | 22528
90 | 11 | TRANSPORT OF COND DRUM,VCBs upto 10km | Elect | Labour | SWR11860 | 2667 | EA | 29337
91 | 400 | Laying of 33kV 6 Run in AR in CC/BT cmp.cuttng | Elect | Labour | SWR12069 | 1815 | M | 726000
92 | 430 | Laying of 33kV 5 Run in HG | Elect | Labour | SWR12053 | 1045 | M | 449350
93 | 200 | Laying of 33kV 5 Run in Xing in CC/BT cmp.cuttng | Elect | Labour | SWR12061 | 1870 | M | 374000
94 | 820 | Laying of 33kV 5 Run in AR in CC/BT cmp.cuttng | Elect | Labour | SWR12057 | 1705 | M | 1398100
95 | 1000 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 91 | M | 91000
96 | 300 | Laying 33kV D.Run Xing in CC/BT cmp.cuttng | Elect | Labour | SWR11988 | 1240 | M | 372000
97 | 1560 | Laying 33kV D.Run AR in CC/BT cmp.cuttng | Elect | Labour | SWR11980 | 1085 | M | 1692600
98 | 400 | Laying 33kV D.Run HG | Elect | Labour | SWR11972 | 585 | M | 234000
99 | 290 | Laying 33kV D.Run Hard Rock | Elect | Labour | SWR11002 | 1430 | RMT | 414700
100 | 2690 | Laying of 2nd cable in excavated trench | Elect | Supply | SWR10988 | 91 | M | 244790
101 | 70 | Laying 33kV 3.Run xing in CC/BT cmp.cuttng | Elect | Supply | SWR12024 | 1552 | M | 108640
102 | 70 | Laying of 2nd cable in excavated trench | Elect | Supply | SWR10988 | 91 | M | 6370
103 | 305 | Raising of 33 KV 3x400 Sqmm Cable on support | Elect | Labour | SWR12004 | 254 | M | 77470
104 | 16 | Outdoor end termination 33kv 3x400 xlpe | Elect | Labour | SWR10387 | 2310 | EA | 36960
105 | 4 | Indoor end termination 33kv 3x400 xlpe | Elect | Labour | SWR10387 | 2310 | EA | 9240
106 | 40 | Straight through joint 33kv 3x400 xlpe | Elect | Labour | SWR10382 | 4764 | EA | 190560
107 | 400 | Supply of 250 mm Hume pipe of class NP3 | Elect | Labour | SMR40077 | 363 | M | 145200
108 | 1000 | Supply of 6" B class GI pipe | Elect | Labour | SMR40081 | 1044 | M | 1044000
109 | 200 | Supply of 6" DWC pipe | Elect | Labour | SMR11610 | 1012 | M | 202400
110 | 4 | LOADING of 33 KV AB SWCH Con 400/800 A | Elect | Labour | SWR10239 | 126 | EA | 504
111 | 4 | UNLOADING of 33 KV AB SWCH Con 400/800 A | Elect | Labour | SWR10557 | 79 | EA | 316
112 | 4 | Erection of 33kv ABSwitch incl earthing | Elect | Labour | SWR10392 | 2048.16 | EA | 8192.64
113 | 9 | Erection of Box Pole | Elect | Labour | SWR11266 | 2048 | EA | 18432
114 | 18 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 1368
115 | 18 | Unloading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 900
116 | 18 | Coping&muffing of iron poles | Elect | Labour | SWR11890 | 3893 | M3 | 70074
117 | 18 | Painting of RS Joist(1C RO, 2C Al.Paint) | Elect | Labour | SWR10640 | 951 | EA | 17118
118 | 18 | Fabrication of 175x85/150x75mm RS joist | Elect | Labour | SWR10642 | 402 | EA | 7236
119 | 7.92 | PCC 1:3:6 using 40mm metal | Elect | Labour | SWR33029 | 5363 | M3 | 42474.96
120 | 7.92 | Earth work excav for founda lead&lifts | Elect | Labour | SWR10857 | 331 | M3 | 2621.52
121 | 60 | Laying of earth mat,excavation 25x3mm | Elect | Labour | SWR10921 | 68 | RMT | 4080
122 | 4 | Coil earthing of pole with No.8 GI wire | Elect | Labour | SWR22091 | 386 | EA | 1544
123 | 4 | Supply of CI pipe of 100 mm dia 2.75 mtr | Elect | Supply | SMR11482 | 3486 | EA | 13944
124 | 4 | Errection of CI Earth pit as per IS3043 | Elect | Supply | SWR10923 | 2122 | EA | 8488
125 | 1 | TRANSPORT OF COND DRUM,VCBs upto 10km | Elect | Supply | SWR11860 | 2667 | EA | 2667
126 | 0.8 | Stringing 100sqmm 33/11kv Line 3 Cond SC | Elect | Labour | SWR10366 | 13585 | KM | 10868
127 | 5 | Horizontal Cut point for 33 KV line | Elect | Labour | SWR10981 | 1756 | EA | 8780
128 | 1 | LOADING of Conductor drums | Elect | Labour | SWR10191 | 202 | EA | 202
129 | 1 | UNLOADING of Conductor drums | Elect | Labour | SWR10509 | 97 | EA | 97
130 | 57 | LOADING of 33 KV Pin insulators | Elect | Labour | SWR10211 | 2.73 | CRT | 155.61
131 | 57 | UNLOADING of 33 KV Pin insulators | Elect | Labour | SWR10529 | 2.73 | CRT | 155.61
132 | 1 | LOADING of 33KV Metal parts-bag of 25no | Elect | Labour | SWR10618 | 65 | BAG | 65
133 | 1 | UNLOADING of 33 KV Metal parts-bagof 25 | Elect | Labour | SWR10632 | 65 | BAG | 65
134 | 20 | Erection of Spun poles 12.5 Mtrs | Elect | Labour | SWR10350 | 4433 | EA | 88660
135 | 20 | Transport of 12.5 Mtrs Spun poles | Elect | Labour | SWR11181 | 858 | EA | 17160
136 | 20 | LOADING of Spun poles 12.5 Mtrs | Elect | Labour | SWR10190 | 548 | EA | 10960
137 | 20 | UNLOADING of Spun poles 12.5 Mtrs | Elect | Labour | SWR10508 | 363 | EA | 7260
138 | 60 | Fabrication of Back clamps with 75 x 8 mm MS Flat . | Elect | Labour | SWR10319 | 31 | EA | 1860
139 | 60 | Fab V.Cross arms with 100x50 mm MS Channel 33Kv | Elect | Labour | SWR10312 | 152 | EA | 9120
140 | 30 | Earth work excav for founda lead&lifts | Elect | Labour | SWR10857 | 331 | M3 | 9930
141 | 2 | S-M+3 Tower Galv | Elect | Labour | SMR11683 | 127700 | EA | 255400
142 | 2 | Erect M+3 Tower Galv | Elect | Labour | SWR11850 | 63309 | EA | 126618
143 | 9.5 | Excvt Pit Hard w/o Blst 1.2mX1.2MX3.3M | Elect | Labour | SWR12090 | 5189 | EA | 49295.5
144 | 29 | Line2\\Load-11KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 29696
145 | 29 | Unload-11KV XLPE UG Cable all sizes | Elect | Labour | SWR11231 | 1024 | DR | 29696
146 | 15 | TRANSPORT OF COND DRUM,VCBs upto 10km | Elect | Labour | SWR11860 | 2667 | EA | 40005
147 | 450 | Laying 11kV 300 S.Run AR in CC/BT cm.ctg | Elect | Supply | SWR11928 | 839 | M | 377550
148 | 50 | Laying 11kV 300Xing S.Rn CC/BT comp.cutt | Elect | Labour | SWR11937 | 937 | M | 46850
149 | 100 | Laying 11KV300 S.Run AR in HG | Elect | Labour | SWR11919 | 363 | M | 36300
150 | 400 | Laying 11kV 300D.Run AR in CC/BT cmp.cut | Elect | Supply | SWR11981 | 988 | M | 395200
151 | 100 | Laying of 11kV UG 2Run in Hard rock. | Elect | Labour | SWR11004 | 1194 | RMT | 119400
152 | 150 | Layin11KV300sqmm D.Run AR in HG | Elect | Labour | SWR11973 | 493 | M | 73950
153 | 650 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 91 | M | 59150
154 | 50 | Laying 11KV300 3Run AR in HG | Elect | Labour | SWR12014 | 612 | M | 30600
155 | 200 | Laying 11kV 300 3.Run AR in CC/BT cm.ctg | Elect | Supply | SWR12020 | 1238 | M | 247600 | 201
156 | 70 | Laying 11kV 300 3.Run XING in CC/BT cm.ctg | Elect | Labour | SWR12025 | 1416 | M | 99120
157 | 640 | Laying of 2nd cable in excavated trench | Elect | Supply | SWR10988 | 91 | M | 58240
158 | 150 | Laying 11kV 300 6.Run AR in CC/BT cm.ctg | Elect | Labour | SWR12070 | 1705 | M | 255750
159 | 100 | Laying 11KV300 6Run in HG | Elect | Supply | SWR12066 | 990 | M | 99000
160 | 1250 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 91 | M | 113750
161 | 70 | Laying of 2nd cable in excavated trench ( 1 Run in 33KV 3Runs Trench ) | Elect | Labour | SWR10988 | 91 | M | 6370
162 | 4800 | Laying of 2nd cable in excavated trench(4 Run in 33KV 5Run Trench) | Elect | Supply | SWR10988 | 91 | M | 436800
163 | 2000 | Laying of 2nd cable in excavated trench(5 Run in 33KV 6Run Trench) | Elect | Labour | SWR10988 | 91 | M | 182000
164 | 270 | Raising of UG Cable 11 KV 3x300 Sqmm | Elect | Labour | SWR11955 | 113 | M | 30510
165 | 20 | OD/Idoor end termination 11kv 3x300 xlpe | Elect | Labour | SWR10391 | 2021 | EA | 40420
166 | 50 | Straight through joint 11kv 3x300 xlpe | Elect | Labour | SWR10386 | 3176 | EA | 158800
167 | 300 | Supply of 150 mm Hume pipe of class NP3 | Elect | Labour | SMR40078 | 303 | M | 90900
168 | 900 | Supply of 4" B class GI pipe | Elect | Labour | SMR40080 | 740 | M | 666000
169 | 600 | Supply of 4" DWC pipe | Elect | Labour | SMR11609 | 759 | M | 455400
170 | 5400 | Consult charg for providng traffic diver | Elect | Labour | SWR21903 | 30 | M | 162000
171 | 5400 | Consultation charges for pursuing with v | Elect | Labour | SWR11801 | 30 | M | 162000
172 | 8 | LOADING of 11 KV AB SWCH Con 200/400 A | Elect | Labour | SWR10238 | 80 | EA | 640
173 | 8 | UNLOADING of 11 KV AB SWCH Con 200/400 A | Elect | Labour | SWR10556 | 80 | EA | 640
174 | 8 | Coil earthing of pole with No.8 GI wire | Elect | Labour | SWR22091 | 386 | EA | 3088
175 | 8 | Supply of CI pipe of 100 mm dia 2.75 mtr | Elect | Labour | SMR11482 | 3486 | EA | 27888
176 | 8 | Errection of CI Earth pit as per IS3043 | Elect | Labour | SWR10923 | 2122 | EA | 16976
177 | 8 | Erection of 11kv ABSwitch incl earthing | Elect | Labour | SWR10393 | 1598.34 | EA | 12786.72
178 | 7.04 | PCC 1:3:6 using 40mm metal | Elect | Labour | SWR33029 | 5363 | M3 | 37755.52
179 | 7.04 | Earth work excav for founda lead&lifts | Elect | Supply | SWR10857 | 331 | M3 | 2330.24
180 | 8 | Fabrication of 175x85/150x75mm RS joist | Elect | Labour | SWR10642 | 402 | EA | 3216
181 | 8 | Erection of Box Pole | Elect | Labour | SWR11266 | 2048 | EA | 16384
182 | 16 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 1216
183 | 16 | Unloading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 800
184 | 16 | Coping&muffing of iron poles | Elect | Labour | SWR11890 | 3893 | M3 | 62288
185 | 16 | Painting of RS Joist(1C RO, 2C Al.Paint) | Elect | Supply | SWR10640 | 951 | EA | 15216
186 | 1 | TRANSPORT OF COND DRUM,VCBs upto 10km | Elect | Supply | SWR11860 | 2667 | EA | 2667
187 | 100 | Laying of earth mat,excavation 25x3mm | Elect | Supply | SWR10921 | 68 | RMT | 6800
188 | 18 | LOADING of 11 KV - Cross arms | Elect | Supply | SWR10228 | 3 | EA | 54
189 | 18 | UNLOADING of 11 KV Cross arms | Elect | Supply | SWR10546 | 3 | EA | 54
190 | 6 | Cut point for 11 KV line | Elect | Supply | SWR10653 | 1119 | EA | 6714
191 | 0.7 | Stringing of 55 Sqmm Single Circuit (3 Conductors) | Elect | Supply | SWR10365 | 7469 | KM | 5228.3
192 | 8.8 | Earth work excav for founda lead&lifts 11KV | Elect | Labour | SWR10857 | 331 | M3 | 2912.8
193 | 42 | LOADING of 11 KV Pin insulators | Elect | Labour | SWR10212 | 1.05 | CRT | 44.1
194 | 42 | UNLOADING of 11 KV Pin insulators | Elect | Supply | SWR10530 | 1.05 | CRT | 44.1
195 | 24 | LOADING of 11 KV Disc insulators | Elect | Labour | SWR12416 | 1.84 | CRT | 44.16
196 | 24 | UNLOADING of 11 KV Disc insulators | Elect | Supply | SWR10631 | 1.84 | CRT | 44.16
197 | 1 | LOADING of 11KV Metal parts-bag of 50no | Elect | Labour | SWR12402 | 48 | BAG | 48
198 | 1 | UNLOADING of 11 KV Metal parts-bagof 50 | Elect | Labour | SWR12421 | 48 | BAG | 48
199 | 38 | Fabrication of Back clamps with 75 x 8 mm MS Flat | Elect | Labour | SWR10319 | 31 | EA | 1178
200 | 30 | Fab V.Cross arms with 100x50 mm MS Channel 11Kv | Elect | Labour | SWR10312 | 152 | EA | 4560
201 | 10 | Erection of 9.1 Pscc Poles | Elect | Labour | SWR10343 | 1621 | EA | 16210
202 | 6 | Erection of Strut pole 9.1pscc pole | Elect | Labour | SWR11083 | 1621 | EA | 9726
| Sub Total: | [6 empty] | 14880866.18
| 18% Service tax on labour | [6 empty] | 2678555.9124
| Total Rs. | [6 empty] | 17559422.0924

## ADITYA EMPRESS TOWERS (hidden)
SCHEDULE
Name of the Work : Erection of 33/11KV Indoor Substation with 2Nos. 12.5 MVA Power Transformers at SANDHYA HOTELS Opp Sunshine Hospitals Raidurgam under T&D Improvement Works.
WBS Element : S-1547-12-01-03-01-001
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 1 | Erection of Three Phase DTRs | Elect | Labour | SWR10463 | 1524 | EA | 1524
2 | 1 | LOADING of 15&25kva DTR | Elect | Labour | SWR10194 | 135 | EA | 135
3 | 1 | UNLOADING of 15&25kva DTR | Elect | Labour | SWR10512 | 135 | EA | 135
4 | 1 | Construction of DTR column for 33/11kV Sub-station as per the DATA-XI | Elect | Labour | SWR22055 | 28861 | EA | 28861
5 | 1 | Erection of 11 KV HG Fuse set including earthing | Elect | Labour | SWR10395 | 660 | SET | 660
6 | 1 | LOADING of 11 KV HG Fuse Sets | Elect | Labour | SWR10231 | 18 | EA | 18
7 | 1 | UNLOADING of 11 KV HG Fuse Sets | Elect | Labour | SWR10549 | 18 | EA | 18
8 | 1 | Erection of 11 KVAB Switch 400/200 A conventional type including alignment and earthing | Elect | Labour | SWR10393 | 1641 | EA | 1641
9 | 1 | LOADING of 11 KV AB Switch Tilting type | Elect | Labour | SWR10237 | 82 | SET | 82
10 | 1 | UNLOADING of 11 KV AB Switch Tilting type | Elect | Labour | SWR10555 | 82 | SET | 82
11 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc (Excluding material) | Elect | Labour | SWR10674 | 1242 | EA | 1242
12 | 90 | Laying of In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-LT 3 1/2 x 185/120/95/70/50 Sqmm Cable in Single Run | Elect | Labour | SWR10433 | 295 | M | 26550
13 | 10 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) -LT 3 1/2 x 185/120/95/70/50 Sqmm Cable | Elect | Labour | SWR10452 | 67 | M | 670
14 | 2 | Making of Outdoor/Indoor end termination LT 3 1/2 x 185 | Elect | Labour | SWR10765 | 809 | EA | 1618
15 | 50 | Excavation & laying of UG Cable in Single Run,In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road,11 KV 3x35 Sqmm Cable | Elect | Labour | SWR20855 | 339 | M | 16950
16 | 15 | Raising of UG Cable 11 KV 3x35 Sqmm 3 | Elect | Labour | SWR10451 | 87 | M | 1305
17 | 1 | Making of Outdoor/Indoor End Termination,11 KV 3x35 Sqmm Cable | Elect | Labour | SWR10388 | 1444 | EA | 1444
18 | 7.5 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3597 | TO | 26977.5
19 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) | Elect | Labour | SWR10139 | 2667 | KM | 2667
20 | 2 | Erection of 12.5 MVA PTR. | Elect | Labour | SWR10929 | 51818 | EA | 103636
21 | 2 | Transport of 12.5MVA power transformer | Elect | Labour | SWR10855 | 27431 | EA | 54862
22 | 2 | LOADING of 12.5 MVA PTR | Elect | Labour | SWR10614 | 12128 | EA | 24256
23 | 2 | UNLOADING of 12.5 MVA PTR | Elect | Labour | SWR10628 | 12128 | EA | 24256
24 | 1 | Loading 220 V Battery with Charger | Elect | Labour | SWR11166 | 1692 | SET | 1692
25 | 1 | Un-loading 220 V Battery with Charger | Elect | Labour | SWR11147 | 1075 | SET | 1075
26 | 1 | Erection of 220V Battery with charger incl eart | Elect | Labour | SWR21896 | 7666 | EA | 7666
27 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) | Elect | Labour | SWR10139 | 2667 | KM | 2667
28 | 16 | Erection of 11KV indoor switchgear panel | Elect | Labour | SWR10931 | 8894 | EA | 142304
29 | 16 | Loading of 11 KV VCBs&Panel boards | Elect | Labour | SWR10199 | 1075 | EA | 17200
30 | 16 | Unloading of 11 KV VCBs&Panel boards | Elect | Labour | SWR10517 | 1075 | EA | 17200
31 | 10 | Erection of 33KV indoor switch gear panel/33KV indoor PT panel / Bus section panel / Bus raiser panel | Elect | Labour | SWR10930 | 9847 | EA | 98470
32 | 10 | LOADING of 33 KV VCBs&Panel boards | Elect | Labour | SWR10198 | 1075 | EA | 10750
33 | 10 | UNLOADING of 33 KV VCBs&Panel boards | Elect | Labour | SWR10516 | 1075 | EA | 10750
34 | 26 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) | Elect | Labour | SWR10139 | 2667 | KM | 69342
35 | 6 | Erection of RS Joist Girder pole 150X150mm | Elect | Labour | SWR10348 | 1407 | EA | 8442
36 | 8 | Erection of RS Joist 175 x 85 mm | Elect | Labour | SWR10346 | 1690.5 | EA | 13524
37 | 17.6 | Laying of foudation with RCC for VCB Plinths (33KV, 11KV & PTR Plinth), as per the drawing (2.2 X 2.2 X 1.5 mtrs), Providing of Concreting (2 X 2 X 1.5 mtrs) with 1:3:6 Concrete mix, size provinding of concreting for PTR ( 3.0M x 3.0M x 1.65M)is as shown in the drawings, Providing the foundation boils (20mm) suitable to VCB Structure plastering of the plinth for smooth finishing with 12mm thick 1:2 cement mortor and providing two coats of white washing for part of te plinth above ground level | Elect | Labour | SWR30007 | 5788 | M3 | 101868.8
38 | 17.6 | Earth work excavation for foundation of VCB etc | Elect | Labour | SWR10857 | 331 | M3 | 5825.6
39 | 7.5 | Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 16357.5
40 | 7.5 | Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 6382.5
41 | 7.5 | Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elect | Supply | SMR40010 | 1293 | TO | 9697.5
42 | 7.5 | Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Elect | Labour | SWR10879 | 482 | TO | 3615
43 | 50 | Painting of Name Plates for any equipment | Elect | Labour | SWR10963 | 122 | EA | 6100
44 | 1 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 142
45 | 6 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. | Elect | Supply | SMR40051 | 14609 | EA | 87654
46 | 6 | Errection of tubular poles | Elect | Labour | SWR10955 | 1379 | EA | 8274
47 | 6 | Supply of 150 W Metal halide lamps with fixtures.. | Elect | Supply | SMR40056 | 6450 | EA | 38700
48 | 6 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. | Elect | Labour | SWR10956 | 1268 | EA | 7608
49 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. | Elect | Supply | SMR40033 | 5209 | EA | 10418
50 | 1700 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Elect | Labour | SWR21301 | 14 | LS | 23800
51 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. | Elect | Supply | SMR40045 | 44100 | EA | 44100
52 | 1 | Erection of control/Relay panels, AC Panels, announciation panels etc in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts. | Elect | Supply | SWR21311 | 2122 | LS | 2122
53 | 750 | Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions | Elect | Supply | SWR10873 | 83 | KG | 62250
54 | 12 | Supply Rubber mats( 6#x3#)size for indoorSS | Elect | Supply | SMR40068 | 1455 | EA | 17460
55 | 1 | Sup Alluminium Ladder for indoor works | Elect | Supply | SMR40062 | 4410 | EA | 4410
56 | 2 | Supply of TrollyMounted Co2 Cylinders(IS-2878) | Elect | Supply | SMR40087 | 9702 | EA | 19404
57 | 2 | Supply of Fire Buckets Stand with Buckets | Elect | Supply | SMR40088 | 1455 | SET | 2910
58 | 6 | Supply of Fire Extinguisher for Control Room | Elect | Supply | SMR40089 | 4851 | EA | 29106
59 | 4 | Supply of Safety Helmet of standard make | Elect | Supply | SMR40071 | 243 | EA | 972
60 | 4 | Supply Earth Rods (8ft) Screw & clamp type | Elect | Supply | SMR40066 | 607 | EA | 2428
61 | 4 | Supply of Hand Gloves | Elect | Supply | SMR40067 | 331 | SET | 1324
62 | 1 | Supply of Stand basic cell phone with charger | Elect | Supply | SMR40069 | 1455 | EA | 1455
63 | 1 | Supply of Steel almarah(61/2 X 3ft) Godrej | Elect | Supply | SMR40061 | 11339 | EA | 11339
64 | 1 | Supply of Table (3x6ft) Godrej | Elect | Supply | SMR40057 | 6671 | EA | 6671
65 | 4 | Supply of S type chairs (Godrej) | Elect | Supply | SMR40058 | 1067 | EA | 4268
66 | 1 | Supply of Angle racks(18x36.6inches) Godrej | Elect | Supply | SMR40060 | 2001 | EA | 2001
67 | 10 | Supply of Danger boards with clamps | Elect | Supply | SMR40070 | 122 | EA | 1220
68 | 1 | Supply of Name board of the 33/11kV Sub-Station(As per Standard Specification) | Elect | Supply | SMR40086 | 10750 | EA | 10750
69 | 1 | Supply of Wall clock standard make | Elect | Supply | SMR40059 | 667 | EA | 667
70 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579-1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. | Elect | Supply | SMR40063 | 9096 | SET | 9096
71 | 1 | Supply of Rechargeable LED torch light. | Elect | Supply | SMR40064 | 1820 | EA | 1820
72 | 1 | Supply of Hack saw (12 inches) | Elect | Supply | SMR40065 | 303 | EA | 303
73 | 8 | Supply of LC Boards | Elect | Supply | SMR40072 | 122 | EA | 976
74 | 2 | Supply of Gum Boots | Elect | Supply | SMR40073 | 728 | EA | 1456
75 | 1 | Supply of Digital clamp meter. | Elect | Supply | SMR40076 | 3032 | EA | 3032
76 | 1 | Supply of 5000v megger | Elect | Supply | SMR40074 | 14553 | EA | 14553
77 | 1 | Supply of Aluminium ladder(10 feet) | Elect | Supply | SMR40007 | 1654 | EA | 1654
78 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard | Elect | Labour | SWR20032 | 1654 | EA | 1654
79 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Elect | Labour | SWR22090 | 2205 | EA | 2205
80 | 36 | Cost of CI earth pipe 100 mm dia, 2.75 mt long with flange | Elect | Supply | SMR11482 | 3494 | EA | 125784
81 | 36 | Excavation of earth pit, putting cast iron pipe with flange on one end of nominal dia 100mm and 2.75 meters long in side the pit including supply and fixing RCC collars 0.75 meter dia (OD), 50mm thick and 0.60meters long in side the pit, backfill the pit with bentonite & black cotton soil mix for full depth of the pit with alternate layers of of 300mm thick around the earth pipe of 150mm on all the sides of the pipe including cost and conveyance of bentonite, Black cotton soil, clamps, C.I.Pipes and RCC collars, labour charges for all operational and incidental items of work etc., complete. | Elect | Labour | SWR10923 | 2122 | EA | 76392
82 | 2 | Excavation of earth pit, putting GI pipe with suitable clamp of nominal dia 40mm and 2.0meters long in side the pit including supply and fixing RCC collars 0.75 meter dia (OD), 50mm thick and 0.60meters long in side the pit, backfill the pit with bentonite & black cotton soil mix for full depth of the pit with alternate layers of of 300mm thick around the earth pipe of 150mm on all the sides of the pipe including cost and conveyance of bentonite, Black cotton soil, clamps, G.I.Pipe and RCC collars, labour charges for all operational and incidental items of work etc., complete. | Elect | Labour | SWR20182 | 1152 | EA | 2304
83 | 2 | Supply of GI eath pipe with 40 mm dia,3mm thcikness with 2.0 M Length | Elect | Supply | SMR11480 | 733 | EA | 1466
84 | 464 | Laying of earth mat at EHT SS -75x 8mm MS Flat / GI Flat. | Elect | Labour | SWR10920 | 68 | RMT | 31552
85 | 375 | Laying of Earth mat 50x6mm Flat | Elect | Labour | SWR21170 | 68 | M | 25500
86 | 500 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Elect | Labour | SWR20813 | 27 | LS | 13500
87 | 2 | Fabrication and laying of ladder in cable trench | Elect | Labour | SWR22088 | 827 | EA | 1654
88 | 10 | Fixing of 105lb rail poles over the transformer plinths. | Elect | Labour | SWR10872 | 471 | RMT | 4710
89 | 34 | Loading of 11/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1075 | DR | 36550
90 | 34 | Unloading of 11/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1075 | DR | 36550
91 | 17 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) upto 10km | Elect | Labour | SWR10139 | 2667 | KM | 45339
Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.
92 | 1100 | Laying of 33 KV 3x400 Sqmm Cable In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC | Elect | Labour | SWR10835 | 585 | M | 643500
93 | 1600 | Laying of 33 KV 3x400 Sqmm Cable Along the CC / BT multi layer road requiring compressor | Elect | Labour | SWR10766 | 1085 | EA | 1736000
94 | 900 | Laying of 33 KV 3x400 Sqmm Cable -Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) | Elect | Labour | SWR10772 | 1240 | EA | 1116000
95 | 1000 | Laying of 33KV XLPE UG cable Double Run of Size in Hard Rock(1.2*0.5x1=0.6cum) | Elect | Labour | SWR11002 | 1430 | RMT | 1430000
96 | 400 | Raising of 33KV XLPE UG cable Double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR22094 | 254 | M | 101600
97 | 4600 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 91 | M | 418600
98 | 22 | Making of 33 KV 3x400 Sqmm Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10387 | 2310 | EA | 50820
99 | 22 | Making of 33 KV 3x400 Sqmm Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10387 | 2310 | EA | 50820
100 | 60 | Making of 33 KV 3x400 Sqmm Cable Straight through joints kits | Elect | Labour | SWR10382 | 4764 | EA | 285840
101 | 1600 | Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | Elect | Supply | SMR40077 | 363 | M | 580800
102 | 3500 | Supply of 6" B class GI pipe | Elect | Supply | SMR40081 | 1044 | M | 3654000
103 | 1500 | Supply of 6" DWC pipe | Elect | Supply |  | 1012 | M | 1518000
104 | 28 | Loading of 11/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1075 | DR | 30100
105 | 28 | Unloading of 11/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1075 | DR | 30100
106 | 14 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) upto 10km | Elect | Labour | SWR10139 | 2667 | KM | 37338
Laying of XLPE UG cable Triple or more Run including excavation of trench of size 1000mm wide to 750mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.
107 | 250 | Laying 11KV XLPE UG Cable Triple run and above in Hard rock | Elect | Labour |  | 2144 | RMT | 536000
108 | 340 | Laying of 11 KV 3x300 / 3x185 / 3x95 Sqmm Cable, Triple run In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC | Elect | Labour | SWR22071 | 612 | M | 208080
109 | 260 | Laying of 11 KV 3x300 / 3x185 / 3x95 Sqmm Cable, Triple run Along the CC / BT multi layer road requiring compressor | Elect | Labour | SWR22075 | 1238 | M | 321880
110 | 150 | Laying of 11 KV 3x300 / 3x185 / 3x95 Sqmm Cable, Triple run Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) | Elect | Labour | SWR22079 | 1416 | M | 212400
111 | 2000 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 91 | M | 182000
Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.
112 | 450 | Laying of 11 KV 3x300 / 3x185 / 3x95 Sqmm Cable, Double run Along the CC / BT multi layer road requiring compressor | Elect | Labour | SWR10767 | 988 | EA | 444600
113 | 210 | Laying of 11 KV 3x300 / 3x185 / 3x95 Sqmm Cable, Double run Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) | Elect | Labour | SWR10773 | 1132 | EA | 237720
114 | 350 | Laying of11KV XLPE UG cable Double Run of Size in Hard Rock(1.05*0.5x1=0.525cum) | Elect | Labour | SWR11004 | 1194 | RMT | 417900
115 | 190 | Laying of 11 KV 3x300 / 3x185 / 3x95 Sqmm Cable, Double run In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC | Elect | Labour | SWR10836 | 493 | M | 93670
116 | 1200 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 91 | M | 109200
Laying of XLPE UG cable Single Run including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.
117 | 1150 | Laying of 11 KV 3x300 / 3x185 / 3x95 Sqmm Cable, Single run Along the CC / BT multi layer road requiring compressor | Elect | Labour | SWR10747 | 839 | M | 964850
118 | 730 | Laying of 11 KV 3x300 / 3x185 / 3x95 Sqmm Cable, Single run Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) | Elect | Labour | SWR10753 | 937 | M | 684010
119 | 470 | Laying of 11KV XLPE UG cable Single Run in Hard Rock(1.05*0.45x1=0.4725cum) | Elect | Labour | SWR11005 | 1075 | RMT | 505250
120 | 250 | Laying of 11 KV 3x300 / 3x185 / 3x95 Sqmm Cable, Single run In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC | Elect | Labour | SWR20846 | 363 | M | 90750
121 | 500 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) -11 KV 3x300 Sqmm Cable | Elect | Labour | SWR10448 | 113 | M | 56500
122 | 35 | Making of 11 KV 3x300 Sqmm Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10391 | 2021 | EA | 70735
123 | 42 | Making of 11 KV 3x300 Sqmm Cable Straight through joints kits | Elect | Labour | SWR10386 | 3176 | EA | 133392
124 | 1000 | Supply of 150 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | Elect | Supply | SMR40078 | 303 | M | 303000
125 | 800 | Supply of 4" B class GI pipe | Elect | Supply | SMR40080 | 740 | M | 592000
126 | 600 | Supply of 4" DWC pipe | Elect | Supply |  | 759 | M | 455400
127 | 9000 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 270000
128 | 9000 | Consultation charges for pursuing with various Departments for obtaining required permissions for Road cutting and submission of necessry Documents, Drawings etc. | Elect | Labour |  | 30 | M | 270000
129 | 9 | LOADING of 11 KV AB Switch Con 200/400 A | Elect | Labour | SWR10238 | 82 | EA | 738
130 | 9 | UNLOADING of 11 KV AB Switch Con 200/400 A | Elect | Labour | SWR10556 | 82 | EA | 738
131 | 6 | LOADING of 33 KV AB Switch Con 400/800 A | Elect | Labour | SWR10239 | 146 | EA | 876
132 | 6 | UNLOADING of 33 KV AB Switch Con 400/800 A | Elect | Labour | SWR10557 | 91 | EA | 546
133 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) upto 10km | Elect | Labour | SWR10139 | 2667 | KM | 2667
134 | 6 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 2103 | EA | 12618
135 | 9 | Erection of 11 KVAB Switch 400/200 A conventional type including alignment and earthing | Elect | Labour | SWR10393 | 1641 | EA | 14769
136 | 8.8 | Laying of foudation with RCC for VCB Plinths (33KV, 11KV & PTR Plinth), as per the drawing (2.2 X 2.2 X 1.5 mtrs), Providing of Concreting (2 X 2 X 1.5 mtrs) with 1:3:6 Concrete mix, size provinding of concreting for PTR ( 3.0M x 3.0M x 1.65M)is as shown in the drawings, Providing the foundation boils (20mm) suitable to VCB Structure plastering of the plinth for smooth finishing with 12mm thick 1:2 cement mortor and providing two coats of white washing for part of te plinth above ground level | Elect | Labour | SWR30007 | 5788 | M3 | 50934.4
137 | 8.8 | Earth work excavation for foundation of VCB etc | Elect | Labour | SWR10857 | 331 | M3 | 2912.8
138 | 5 | Coping&muffing of iron poles | Elect | Labour | SWR20584 | 3893 | EA | 19465
139 | 5 | Fabrication of Box pole | Elect | Labour | SWR20749 | 615 | EA | 3075
140 | 5 | Erection of Box Pole | Elect | Labour | SWR20587 | 2257.5 | EA | 11287.5
141 | 5 | LOADING of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 73 | EA | 365
142 | 5 | UNLOADING of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 49 |  | 245
143 | 5 | Painting of RS Joist(1C RO, 2C Al.Paint) | Elect | Labour | SWR10640 | 1149 | EA | 5745
144 | 9 | Excavation of earth pit, putting GI pipe with suitable clamp of nominal dia 40mm and 2.0meters long in side the pit including supply and fixing RCC collars 0.75 meter dia (OD), 50mm thick and 0.60meters long in side the pit, backfill the pit with bentonite & black cotton soil mix for full depth of the pit with alternate layers of of 300mm thick around the earth pipe of 150mm on all the sides of the pipe including cost and conveyance of bentonite, Black cotton soil, clamps, G.I.Pipe and RCC collars, labour charges for all operational and incidental items of work etc., complete. | Elect | Labour | SWR20182 | 1152 | EA | 10368
145 | 9 | Supply of GI pipe of 40 mm dia 2 mtrs | Elect | Supply | SMR40091 | 667 | EA | 6003
146 | 450 | Laying of earth mat,excavation 25x3mm | Elect | Labour | SWR10921 | 81 | RMT | 36450
147 | 11 | Coil earthing of pole with No.8 GI wire | Elect | Labour | SWR22091 | 386 | EA | 4246
148 | 2 | Cost of CI earth pipe 100 mm dia, 2.75 mt long with flange | Elect | Supply | SMR11482 | 3494 | EA | 6988
149 | 2 | Excavation of earth pit, putting cast iron pipe with flange on one end of nominal dia 100mm and 2.75 meters long in side the pit including supply and fixing RCC collars 0.75 meter dia (OD), 50mm thick and 0.60meters long in side the pit, backfill the pit with bentonite & black cotton soil mix for full depth of the pit with alternate layers of of 300mm thick around the earth pipe of 150mm on all the sides of the pipe including cost and conveyance of bentonite, Black cotton soil, clamps, C.I.Pipes and RCC collars, labour charges for all operational and incidental items of work etc., complete. | Elect | Labour | SWR10923 | 2122 | EA | 4244
150 | 6 | Const. of plinth for mount new 3Way RMU | Elect | Labour |  | 6540 | EA | 39240
151 | 6 | Erection of 11KV 3 Way RMU | Elect | Labour | SWR10664 | 1322.5 | EA | 7935
152 | 5 | Erection of RS Joist 175 x 85 mm | Elect | Labour | SWR10346 | 1690.5 | EA | 8452.5
153 | 6 | Supply of 33kV TC Structure as per DATA-II | Elect | Supply | SMR40102 | 49708 | EA | 298248 | 201
154 | 6 | Erection of 33kV TC Structure as per DATA-II | Elect | Labour | SWR11010 | 16240 | EA | 97440
155 | 12 | Supply of 33kV BD Boom as per DATA-IV | Elect | Supply | SMR40104 | 17886 | EA | 214632
156 | 12 | Erection of 33kV BD Boom as per DATA-IV | Elect | Labour | SWR10875 | 495 | EA | 5940
157 | 2 | Supply of 33kV TD Structure as per DATA-I | Elect | Supply | SMR40101 | 20534 | EA | 41068
158 | 2 | Erection of 33kV TD Structure as per DATA-I | Elect | Labour | SWR11009 | 13856 | EA | 27712
159 | 2 | Erection of 33kv ABSwitch incl earthing | Elect | Labour | SWR10392 | 2103 | EA | 4206
160 | 0.2 | Supply of Zebra conductor | Elect | Supply |  | 299369 | KM | 59873.8
161 | 2 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | SET | 1760
162 | 1 | LOADING of 33 KV VCBs&Panel boards | Elect | Labour | SWR10198 | 1075 | EA | 1075
163 | 1 | UNLOADING of 33 KV VCBs&Panel boards | Elect | Labour | SWR10516 | 1075 | EA | 1075
164 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) | Elect | Labour | SWR10139 | 2667 | KM | 2667
165 | 1 | Erection of 33kV Twin feeder control & Relay panel in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Elect | Labour | SWR10934 | 1906 | EA | 1906
166 | 2 | LOADING of 33 KV AB Switch Con 400/800 A | Elect | Labour | SWR10239 | 146 | EA | 292
167 | 2 | UNLOADING of 33 KV AB Switch Con 400/800 A | Elect | Labour | SWR10557 | 91 | EA | 182
168 | 2 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) UPTO 10KM | Elect | Labour | SWR10131 | 303 | TO | 606
169 | 1 | Erection of 33 KV VCB with Control Panel | Elect | Labour | SWR10460 | 5022 | EA | 5022
170 | 1 | Erection of 33kv CT s | Elect | Labour | SWR10399 | 1133 | SET | 1133
171 | 5.4 | Earth work excavation for foundation of VCB etc | Elect | Labour | SWR10857 | 291 | M3 | 1571.4
172 | 7.26 | Laying of foudation with RCC for VCB Plinths (33KV, 11KV & PTR Plinth), as per the drawing (2.2 X 2.2 X 1.5 mtrs), Providing of Concreting (2 X 2 X 1.5 mtrs) with 1:3:6 Concrete mix, size provinding of concreting for PTR ( 3.0M x 3.0M x 1.65M)is as shown in the drawings, Providing the foundation boils (20mm) suitable to VCB Structure plastering of the plinth for smooth finishing with 12mm thick 1:2 cement mortor and providing two coats of white washing for part of te plinth above ground level | Elect | Labour | SWR30007 | 5788 | M3 | 42020.88
173 | 3 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Elect | Labour | SWR10862 | 373 | M2 | 1119
174 | 9 | Conn. of equip/bus single zebra/panther | Elect | Labour | SWR10884 | 224 | EA | 2016
175 | 3 | Supply&Erec of CI earth Pipe as APTRANCO | Elect | Labour | SWR10924 | 10784 | EA | 32352
176 | 60 | Earthing for raisers of SS Flat 50x6 mm. | Elect | Labour | SWR10919 | 41 | RMT | 2460
177 | 520 | SupEarth mat-100X16mm GI Flat-earth pits | Elect | Supply | SMR40093 | 975 | M | 507000
178 | 41 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication.-100x16mm M.S./G.I earth flat | Elect | Labour | SWR22054 | 68 | RMT | 2788
179 | 12 | Hoisting of Insl. 2 Zebra/Phanther 33kV | Elect | Labour | SWR10882 | 1302 | EA | 15624
180 | 18 | With Single Zebra without PASD. | Elect | Labour |  | 338.62 | EA | 6095.16
181 | 3 | With Single Zebra with PASD. | Elect | Labour |  | 828.78 | EA | 2486.34
182 | 3 | With Twin Zebra with PASD. | Elect | Labour |  | 1263.91 | EA | 3791.73
183 | 3 | Supply of Spacer T- clamps -Twin zebra/Panther | Elect | Supply | SMR40012 | 533 | EA | 1599
184 | 3 | Supply of Spacer T-clamps dble dppr zebra/Pant | Elect | Supply | SMR40013 | 827 | EA | 2481
185 | 12 | Supply of Tension Hardw 3 Bolt 2Zebra/panther | Elect | Supply | SMR40016 | 2638 | SET | 31656
186 | 24 | Supply of Pad clamp 75X75X15mm 1 panther 600A | Elect | Supply | SMR40018 | 238 | SET | 5712
187 | 6 | Supply of CT stud clamps 1Zebra/Panth for 800A | Elect | Supply | SMR40023 | 419 | EA | 2514
188 | 6 | Supply of U-Bolts 16 mm | Elect | Supply | SMR40040 | 39 | EA | 234
189 | 1 | Supply of FRP CT Marshalling Box | Elect | Supply | SMR40046 | 4355 | EA | 4355
190 | 1 | Erection of Marshalling boxes | Elect | Labour | SWR10940 | 294 | EA | 294
191 | 100 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Elect | Labour | SWR20813 | 27 | LS | 2700
192 | 2 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. | Elect | Supply | SMR40051 | 14609 | EA | 29218
193 | 2 | Errection of tubular poles | Elect | Labour | SWR10955 | 1379 | EA | 2758
194 | 2 | Supply of 150 W Metal halide lamps with fixtures.. | Elect | Supply | SMR40056 | 6450 | EA | 12900
195 | 1.76 | Earth work excavation for foundation of VCB etc | Elect | Labour | SWR10857 | 331 | M3 | 582.56
196 | 1.76 | Laying of foudation with RCC for VCB Plinths (33KV, 11KV & PTR Plinth), as per the drawing (2.2 X 2.2 X 1.5 mtrs), Providing of Concreting (2 X 2 X 1.5 mtrs) with 1:3:6 Concrete mix, size provinding of concreting for PTR ( 3.0M x 3.0M x 1.65M)is as shown in the drawings, Providing the foundation boils (20mm) suitable to VCB Structure plastering of the plinth for smooth finishing with 12mm thick 1:2 cement mortor and providing two coats of white washing for part of te plinth above ground level | Elect | Labour | SWR30007 | 5877 | M3 | 10343.52
197 | 60 | Labour charges for Fixing of all types of clamps | Elect | Labour | SWR10917 | 65 | EA | 3900
198 | 1000 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Elect | Labour | SWR21301 | 14 | LS | 14000
| Sub Total: | [6 empty] | 22313193.99
| 18% Service tax on labour | [6 empty] | 4016374.9182
| Total Rs. | [6 empty] | 26329568.9082